CENWP-OP-B                                                                                                                         September 01, 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 35 of 2008, which covers the period from 24 August through 30 August 2008.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 121.6 to 157.3 kcfs.  Daily average project tailwater ranged from 11.2’ to 13.6’ msl.  Daily average powerhouse forebay elevation ranged from 75.2’ to 75.8’ msl.  Daily average river temperature ranged from 70°F to 71°F.  Secchi disk measurements ranged from 5.0’ to 7.0’.
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 79.3 to 95.1 kcfs.  Spill for juvenile fish passage is scheduled to end on 31 August.  
1.2.1 Bay 18 remains set at 2 dogs, or 2.9’, while the Bay 15 hoist is being repaired.
1.3 Unit Operation.  Powerhouse 2 is the priority powerhouse.  
1.3.1 Unit 4 went out of service at 0720 on 25 August for BPA switchyard work.
1.3.2 Unit 5 went out of service at 0720 on 25 August for BPA switchyard work.

1.3.3 Unit 6 went out of service at 0720 on 25 August for BPA switchyard work.

1.3.4 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.
1.3.5 Unit 8 went out of service at 0720 on 25 August for BPA switchyard work.
1.3.6 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.7 Unit 11 has remained out of service since 0238 on 12 June due to rotor cracks.
1.3.8 Unit 12 was out of service from 0720 until 2023 on 25 August for BPA switchyard work.

1.3.9 Unit 13 was out of service from 0720 until 2023 on 25 August for BPA switchyard work.

1.3.10 Unit 14 was out of service from 0720 until 2023 on 25 August for BPA switchyard work.

1.3.11 Unit 15 was out of service from 0720 until 2023 on 25 August for BPA switchyard work.

1.3.12 Unit 16 was out of service from 0720 until 2023 on 25 August for BPA switchyard work.

1.3.13 Unit 17 was out of service from 0720 until 2023 on 25 August for BPA switchyard work.

1.3.14 Unit 18 was out of service from 0720 until 2023 on 25 August for BPA switchyard work.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 Fish Unit 1 was out service from 0206 on 25 August until 0226 on 26 August for the RC #3 outage 

              for BPA switchyard work.  
1.4.2 Fish Unit 2 was out of service form 0242 on 25 August until 0230 on 26 August for the RC #3 outage for BPA switchyard work.  

1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System (AWS) Closures.  The following AWS closures occurred this reporting week:
2.1.1 FV 1-1 was closed for cleaning from 0816 until 0842 on 28 August.

2.2 Submersible Traveling Screens (STS)/Vertical Barrier Screens (VBS) inspections.  
The following STS/VBS video inspections occurred this week.  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	8/26
	0
	Out of service

	12
	8/26
	264
	OK

	13
	8/26
	66
	OK

	14
	8/26
	155
	OK

	15
	8/26
	517
	OK

	16
	8/26
	44
	OK

	17
	8/26
	141
	OK

	18
	8/26
	535
	OK


2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this reporting week.
3 RESEARCH  
3.1 Battelle.  Behavioral Guidance System (BGS) hydrophones are installed.  
3.2 Battelle.  Spillway survival evaluation continues.
3.3 CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  Water temps reached 70°F on 08 August.  High temperature sampling protocols remain in effect. 
3.4 CTUIR.  Received 192 lamprey for broodstock and 30 lamprey for radio-tagging from NOAA Fisheries as part of their Umatilla Basin restoration project.
3.5 NOAA – Gilbreath.  Saltwater tag effects study continues.
3.6 NOAA – Moser.  Trapping and PIT tagging at the AFF continues.  
3.7 PSMFC Smolt Monitoring.  Condition, index, and GBT monitoring continue.  No adult salmonids were recorded crossing the separator bars.  Nine juvenile shad were collected for USGS. 
3.8 USGS. Nine juvenile shad were received for the Impacts of American Shad on the Columbia River study.  
3.9 WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.  Tule counting began on 15 August.
3.10 Yakama Nation Fisheries.  Sort by code collection, fat metering, floy tagging, and measuring Wenatchee River coho began this week.

4 FISHWAYS 

4.1 Project biologists inspected on 24-30 August. 
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	8/24, 28
	FG3-27
	Incorrect position
	System in manual
	Ops adjusted
	

	8/30
	BI Weir
	Reading <1.0’
	Unknown
	Ops adjusted
	

	8/30
	B-branch weir
	Reading <1.0’
	Unknown
	Ops adjusted
	

	8/24, 30
	B-branch entrance
	Differential <1.0’
	System in manual
	Ops adjusted
	

	CASCADES ISLAND (CI)

	8/24, 28
	FG6-14
	Incorrect position
	System in manual
	Ops adjusted
	

	8/24
	CI entrance
	Differential <1.0’
	System in manual
	Ops adjusted
	

	WASHINGTON SHORE (WS) 

	8/25
	PH2 entrances
	Differential <1.0’
	Fish units OOS due to line work
	Corrected by 8/26
	


4.2.1 FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is Out of Criteria (OOC) when Tailwater (TW) is above 19.0’ msl.
4.2.2 PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

4.2.3 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.2.4 FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It is OOC when TW is above 16.7’ msl.

4.2.5 PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the Upstream Migrant Transportation (UMT) channel and the main ladder at Washington shore. Daily average temperatures are in Fahrenheit.

4.3.1       Bradford Island temperatures are not available at this time.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA shore
	AFF
	SMF

	8/24
	71.1
	71.2
	70.1

	8/25
	70.9
	71.0
	70.0

	8/26
	70.7
	70.8
	69.7

	8/27
	70.4
	70.5
	69.4

	8/28
	70.1
	70.3
	69.1

	8/29
	70.1
	70.2
	69.2

	8/30
	69.9
	69.9
	69.0


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 29 August.
4.5.2 B-Branch and Cascades Island fishway Program Logic Controls (PLC) are in manual.
4.5.3 Removal of the Floating Orifice Gate (FOG) sea lion exclusion bars has not yet begun due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.  
4.5.4 Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.
4.5.5 PH2 fishway entrances operated as follows during the BPA switchyard work:
From 0345 on 25 August until 0230 on 26 August the SUE, SDE, NUE were closed and the NDE was open 6.0 ft.  Differential was 0.3 ft
4.6 Juvenile Fishways.

4.6.1
   Spill for juvenile fish passage is scheduled to end on 31 August.

4.6.2
   B2CC is scheduled to close on 01 September.
4.7 Lamprey Fishways.  
4.7.1 WS and BI AWS lamprey ramps remain in service.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway (ITS) Wall Removal.  Three automated gates to be installed.  
5.2 TIE crane.  The TIE crane boom repair contract is currently out for bid.

6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 19 June details the start of summer spill for juvenile fish passage.  It supercedes the teletype sent on 10 April. 

7.1.1 From 0001 on 21 July until 2400 on 31 August, Bonneville will spill 75K during daytime hours and to the 120% gas cap at night.

7.1.2 The spill pattern is found in section 2, Table BON-15 of the 2008 FPP, and daytime hours are defined in section 2, Table BON-5 of the 2008 FPP.  www.nwd-wc.usace.army.mil/tmt/documents/fpp/
7.1.3 At no time will the Project voluntarily spill above the 120% gas cap.  The 120% spill cap level for Bonneville can be found in the teletype “SPILL PRIORITY LIST”. 

7.1.4 At all times, maintain a minimum generation of 30kcfs and minimum spill of 50kcfs.

7.2 A teletype sent on 23 June authorizes the Project to dog open Spillbays 11, 14, and 18 at 2 stops (approx. 2.9’).  Spill shall be maintained as specified in 7.1.  This is to facilitate repairs to the Spillbay 15 hoist.  
7.3 A teletype sent on 21 August requests the BON pool be operated with a 1.5’ range hard constraint and a 1.0’ range soft constraint from 0600 on 26 August until 1800 on 29 August.  This operation is intended to hold the pool as steady as possible to minimize debris in the tribal gill nets.
7.4 A teletype sent on 28 August details the end of spill for juvenile fish passage.  Spill is requested to conclude at 0001 on 01 September, and is part of the 2008 FOP.  The B2CC (BON PH2 corner collector) will close beginning at 0630 on 01 September.
7.5 A teletype sent on 29 August requests the BON pool be maintained at 75.0-76.5’ msl hard constraint and 75.5’-76.5’ msl soft constraint from 0600 on 02 September until 1800 on 06 September.  This operation is intended to hold the pool as steady as possible to minimize debris in the tribal gill nets.
7.6 A teletype sent on 29 August requests Bonneville outflows to be maintained as low and as constant as possible from 0700-1130 hours on 01 September.  It is requested that outflows not exceed 150 kcfs.  This operation is to reduce currents during the cross channel swim.

JAMES R. MAHAR, P.E.

Operations Manager
1

