CENWP-OP-B                                                                                                                         September 15, 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 37 of 2008, which covers the period from 07 through 13 September 2008.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 79.8 to 117.0 kcfs.  Daily average project tailwater ranged from 7.7’ to 10.2’ msl.  Daily average powerhouse forebay elevation ranged from 75.9’ to 76.3’ msl.  Daily average river temperature ranged from 68°F to 69°F.  Secchi disk measurements averaged 7.0’.
1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 1.4 to 1.6 kcfs.  
1.3 Unit Operation.  Powerhouse 2 is the priority powerhouse.  
1.3.1 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.2 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.3 Unit 11 has remained out of service since 0238 on 12 June due to rotor cracks.
1.3.4 Unit 13 was out of service from 1207 on 08 September until 1110 on 09 September due to RC#3&4 load limit lowered to 250 MW.
1.3.5 Unit 15 went out of service at 0654 on 05 September due to rotor pole failure.

1.3.6 Unit 16 went out of service at 1950 on 03 September due to RC#3&4 330MW limit.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System (AWS) Closures.  The following AWS closures occurred this reporting week:
2.1.1     FV1-1 was closed for cleaning at 1615 until 1625 on 09 Sept. and from 1520 until 1531 on 11 Sept.
2.1.2     FV3-7 was closed for cleaning at 0701 until 0747 on 10 Sept. 

2.1.3     FV6-9 was closed for cleaning at 1557 until 1602 on 11 Sept.

2.2 Submersible Traveling Screens (STS)/Vertical Barrier Screens (VBS) inspections.  
No STS/VBS video inspections occurred this week.  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11-18
	N/A
	N/A
	N/A


2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this reporting week.
3 RESEARCH  
3.1 Battelle.  Behavioral Guidance System (BGS) hydrophones are installed.  
3.2 Battelle.  Spillway survival evaluation continues.
3.3 CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues. 
3.4 NOAA – Gilbreath.  Saltwater tag effects study continues.
3.5 NOAA – Moser.  Trapping and PIT tagging lamprey at the AFF concluded on 05 September.
3.6 PSMFC Smolt Monitoring.  Condition, index, and GBT monitoring continue.  Five chinook, two steelhead, and one chinook jack (dead on arrival) were recorded crossing the separator bars.  No research fish collected during this report period. 
3.7 USGS. No shad were received for the Impacts of American Shad on the Columbia River study.  
3.8 WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.  Tule counting began on 15 August.
3.9 Yakama Nation Fisheries.  Sort by code collection, fat metering, Floy tagging, and measuring Wenatchee River coho began the week of 24 August.

4 FISHWAYS 

4.1 Project biologists inspected on 07 - 13 September.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	9/8
	B-branch entrance
	Differential >2.0’
	System in manual
	Ops adjusted
	

	9/12
	PH1 south collection channel entrance
	Differential low
	System in manual for low tailwater
	Ops adjusted, returned to auto
	

	CASCADES ISLAND (CI) – Nothing to report

	WASHINGTON SHORE (WS) – Nothing to report


4.2.1 FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is Out of Criteria (OOC) when Tailwater (TW) is above 19.0’ msl.
4.2.2 PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

4.2.3 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.2.4 FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It is OOC when TW is above 16.7’ msl.

4.2.5 PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the Upstream Migrant Transportation (UMT) channel and the main ladder at Washington shore. Daily average temperatures are in Fahrenheit.

4.3.1       Bradford Island temperatures are not available at this time.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA shore
	AFF
	SMF

	9/7
	68.3
	68.4
	67.4

	9/8
	68.3
	68.5
	67.3

	9/9
	68.7
	68.6
	67.5

	9/10
	68.8
	68.8
	67.6

	9/11
	68.5
	68.6
	67.4

	9/12
	68.5
	68.6
	67.4

	9/13
	68.7
	68.7
	67.6


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 12 September.
4.5.2 B-Branch and Cascades Island fishway Program Logic Controls (PLC) are in manual.
4.5.3 Removal of the Floating Orifice Gate (FOG) sea lion exclusion bars has not yet begun due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.  
4.5.4 Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.
4.5.5 Due to salmonid counts at Bonneville exceeding 25,000 per day, units at PH1 were in operation following the guidelines in section BON 2.1.2 of the 2008 Fish Passage Plan.  This operation occurred from 04 until 10 September. 
4.6 Juvenile Fishways.

4.6.1 Spill for juvenile fish passage concluded 01 September.
4.6.2
   B2CC was closed on 01 September.  
4.7 Lamprey Fishways.  
4.7.1 WS and BI AWS lamprey ramps remain in service.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway (ITS) Wall Removal.  Three automated gates to be installed.  
5.2 TIE crane.  The TIE crane boom repair contract is currently out for bid.

6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 05 September requests the BON pool be maintained at 75.0-76.5’ msl hard constraint and 75.5’-76.5’ msl soft constraint from 0600 on 09 September until 1800 on 12 September.  This operation is intended to hold the pool as steady as possible to minimize debris in the tribal gill nets.

7.2 A teletype sent on 10 September gives the project permission to exceed the tailwater limit of 4’ per 24 hour period.  Can exceed up to 5’ in the 24 hour period.  The exceedance is needed to draft water from the lower river in anticipation of the Chief Joseph coffer dam move on 11 September. 

7.3 A teletype sent on 12 September requests that Bonneville pool be operated in a one and one half foot operating range as a hard constraint and a one foot operating range as a soft constraint from 0600 on 15 Sept. until 1800 on 18 Sept.  The goal of this operation is to limit wear and tear on gill net equipment and provide steady pool for fish salvage exercises.  

JAMES R. MAHAR, P.E.

Operations Manager
1

