CENWP-OD-B                                                                                                                                  30 November 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 48 of 2008, which covers the period from 23 through 29 November 2008.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 122.4 to 127.9 kcfs.  Daily average project tailwater ranged from 11.4’ to 11.5’ msl.  Daily average powerhouse forebay elevation ranged from 74.7’ to 75.4’ msl.  Daily average river temperature ranged from 50ºF to 52ºF.  Secchi disk measurements ranged from 5.5’ to 7.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged between 1.1 to 1.2 kcfs.  
1.3 Unit Operation.  Powerhouse 2 is the priority powerhouse.   

1.3.1 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.2 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.3 Unit 11 has remained out of service since 12 June due to rotor cracks.
1.3.4 Unit 15 has remained out of service since 05 September due to rotor pole failure.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed for cleaning this reporting week:
2.1.1 FV1-1- from 1259 until 1343 on 24 November; from 1500 until 1615 on 29 November.
2.1.2 FV3-9- from 1012 until 1028 on 24 November; from 1245 until 1300 on 25 November; from 1451 until 1500 on 29 November.

2.1.3 FV5-9- from 1245 until 1300 on 25 November.

2.1.4 Weir 37 bleed off- from 1845-0445 on 25 November; from 1840-0430 on 26 November.

2.2 STS/VBS inspections.  The following STS/VBS video inspections occurred this reporting week:  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1, 3
	NA
	NA
	Scheduled for removal for the ITS modifications 1 December

	11-17
	NA
	NA
	

	18
	11/25
	
	VBSs cleaned.


2.3 Dewatering and Fish Salvage.  No fish salvage activity occurred this reporting week.
3 RESEARCH  
3.1 WDFW Fish Counting.  Daily video counting at Bradford Island and Washington Shore continues.
4 FISHWAYS 

4.1 Project biologists inspected 23 through 29 November.  NOAA Fisheries inspected on 28 November.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND 

	11/25
	BI exit
	Debris on trashrack
	Debris in river
	Riggers cleaned
	

	11/26,28
	B-branch ent
	Differential high
	System in manual
	Ops adjusted
	

	11/27,28
	PH1 PCC
	Differential low
	System in manual
	Ops adjusted
	

	11/28
	BI weir
	Reading < 1.0
	FV3-7 in manual
	Ops adjusted
	

	11/28
	B-branch weir 
	Reading < 1.0
	FV3-7 in manual
	Ops adjusted
	

	11/28
	Weir 38
	Reading < 1.0
	FV6-9 not controlling properly
	Ops adjusted
	

	11/28
	Weir 67
	Reading < 1.0
	FV 6-9 not controlling properly
	Ops adjusted
	

	CASCADES ISLAND– no out of criteria items 

	WASHINGTON SHORE

	11/24
	Weir 38
	Reading <1.0’>
	FV6-9 in manual
	Ops adjusted
	

	All week
	SA-24 board
	Not reading
	OOS for repairs
	
	


4.2.1 FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is OOC when TW is above 19.0’ msl.
4.2.2 PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

4.2.3 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.2.4 FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It is OOC when TW is above 16.7’ msl.

4.2.5 PH2 velocity meter.  The velocity meter is believed to be broken.  Plans are to replace with a mechanical meter.

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT channel and the main ladder at Washington shore.  Daily average temperatures are in Fahrenheit.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA shore
	Bradford Is.

	11/23
	
	

	11/24
	
	

	11/25
	
	

	11/26
	
	

	11/27
	
	

	11/28
	
	

	11/29
	
	

	11/30
	
	


4.3.1 Temperatures are not available this week due to program upgrades on the new ACE-IT refresh computers.

4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 28 November.
4.5.2 B-Branch and Cascades Island fishway PLCs are in manual.
4.5.3 Due to a broken lifting beam, sea lion exclusion bars remain installed in the four large FOGs.  Stab plates remain installed in the smaller FOGs.  
4.5.4 Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.
4.5.5 STSs were installed on 15 September in Units 1 and 3 for adult fallback.  DSM1 is running south.
4.5.6 FV6-9 was put in manual at 0500 on 23 November.  The valve was not properly controlling in auto.

4.6 Juvenile Fishways.

4.6.1 The JMF went to bypass on 31 October.    
4.6.2 DSM1 orifice lights went off at 1830 on 29 November as prep for the dewatering on 1 December.
4.7 Lamprey Fishways.  BI and WA shore AWS lamprey ramps are winterized.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation in FY09.  Wall removal in FY10.
5.2 TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 06 November establishes the upper BON forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.  

7.2 A teletype sent on 12 November requests BON tailwater operations for chum spawning.  It requests a tailwater elevation hard constraint of a minimum of 11.3’ msl during all hours and between 11.3’ to 11.7’ msl between 0600 and 1800 hours daily.  Target elevation is 11.5’ msl.    
7.3 Winter maintenance is scheduled to begin 1 December.  Bradford Island will go to orifice flow on 1 December and be dewatered on 3 December.  DSM1 screens will be pulled and the DSM will be dewatered on 1 December.  For a complete list of dewatering activities, please contact Project Fisheries.

JAMES R. MAHAR, P.E.

Operations Manager
1

