CENWP-OD-B                                                                                                                                  30 December 2008
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 52 of 2008, which covers the period from 21 through 27 December 2008.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 122.3 to 146.4 kcfs.  Daily average project tailwater ranged from 11.6’ to 13.0’ msl.  Daily average powerhouse forebay elevation ranged from 74.1 to 75.1’ msl.  Daily average river temperature ranged from 39ºF to 40ºF.  Secchi disk measurements were 7.0’.
1.2 Spill Bay 1, which provides attraction flow for Cascades Island, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 0.6 kcfs.  
1.3 Unit Operation.  Powerhouse 2 is the priority powerhouse.   

1.3.1 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.2 Unit 8 has remained out of service since 17 December due to turbine bearing failure.
1.3.3 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.4 Unit 11 has remained out of service since 12 June due to rotor cracks.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 Unit F1 has remained out of service since 01 December for annual maintenance.

1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

2.1.2 FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.

2.2 STS/VBS inspections.  No  STS/VBS video inspections occurred this reporting week.  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1, 3
	NA
	NA
	Scheduled for removal for ITS modifications in late January

	11-18
	NA
	NA
	Removed for season.


2.3 Dewatering and Fish Salvage.  No fish salvage or dewatering activities occurred this week.
3 RESEARCH  
3.1 WDFW Fish Counting.  Daily video counting at Washington Shore continues.  
4 FISHWAYS 

4.1 Project biologists were unable to inspect this reporting week due to inclement weather.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND – OOS for winter maintenance

	CASCADES ISLAND – nothing to report

	All week
	Bonneville
	No inspections done by bios
	Inclement weather
	Inspected on 12/29
	

	Once
	Bonneville
	Calibration not done.
	Inclement weather
	To be done week of 12/28
	

	WASHINGTON SHORE

	All week
	Bonneville
	No inspections done by bios
	Inclement weather
	Inspected on 12/29
	


4.2.1 FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is OOC when TW is above 19.0’ msl.
4.2.2 PH2 velocity meter.  The velocity meter is believed to be broken.  Plans are to replace with a mechanical meter.

4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was not checked this week due to inclement weather.
4.5.2 Cascades Island fishway PLC is in manual.
4.5.3 Due to a broken lifting beam, sea lion exclusion bars remain installed in the four large FOGs.  Stab plates remain installed in the smaller FOGs.  
4.5.4 Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.
4.5.5 STSs were installed on 15 September in Units 1 and 3 for adult fallback.  DSM1 is running south.

4.5.6 FV6-9 was returned to auto at 0030 on 24 December. 

4.5.7 Bradford Island fishway has been out of service since 3 December for winter maintenance.  Flow remains out of FG3-18 to move sturgeon and to prevent a need to unnecessarily handle large numbers of sturgeon.

4.5.8 The Adult Fish Facility went to orifice flow at 1442 on 01 December.  It was scheduled to be dewatered on 22 December but activities were cancelled due to inclement weather.  
4.6 Juvenile Fishways.

4.6.1 DSM1 dewatering has been scheduled for late January.
4.6.2 DSM2 remains dewatered.
4.7 Lamprey Fishways.  BI and WA shore AWS lamprey ramps are winterized.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation in FY09.  Wall removal in FY10.
5.2 TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report this week.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 06 November establishes the upper BON forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.  

7.2 A teletype sent on 16 December replaces the teletype sent on 12 November regarding BON tailwater operations for chum spawning.  It requests a tailwater elevation hard constraint of a minimum of 11.3’ msl during all hours and between 11.3’ to 11.7’ msl between 0600 and 1500 hours daily.  Target elevation is 11.5’ msl.    

7.3 A teletype sent on 22 December requests a minimum Bonneville forebay elevation of 73.4’ msl through 28 December, soft constraint.  This operation was requested by the Port of Cascade Locks in an effort to prevent damage due to ice in the Cascade Locks Marina.

7.4 Winter maintenance began on 1 December.  For a complete list of dewatering activities, please contact Project Fisheries.

JAMES R. MAHAR, P.E.

Operations Manager
1

