CENWP-OD-B                                                                                                                                  09 February 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 6 of 2009, which covers the period from 01 through 07 February 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 122.8 to 152.7 kcfs.  Daily average project tailwater ranged from 11.6’ to 13.5’ msl.  Daily average powerhouse forebay elevation ranged from 74.1’ to 75.0’ msl.  Daily average river temperature was 38ºF.  Secchi disk measurements were between 6.0’ to 7.0’.
1.2 Spill Bay 18, which provides attraction flow for B-Branch, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 0.6 kcfs. 
1.3 Unit Operation.  Powerhouse 1 remains the priority powerhouse.
1.3.1 Unit 1 was out of service from 0839 until 0851 on 02 February for 3D cam testing.

1.3.2 Unit 2 was out of service from 0915 until 0925 on 02 February for 3D cam testing.

1.3.3 Unit 3 was out of service from 0951 until 1002 on 02 February for 3D cam testing.

1.3.4 Unit 4 was out of service from 1024 until 1034 on 02 February for 3D cam testing.

1.3.5 Unit 5 was out of service from 1055 until 1104 on 02 February for 3D cam testing.  U5 was out of service from 0722 until 0802 on 05 February for bank 7/8 switching.

1.3.6 Unit 6 was out of service from 1125 until 1134 on 02 February for 3D cam testing.  U6 was out of service from 0723 until 0804 on 05 February for bank 7/8 switching.

1.3.7 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.8 Unit 8 has remained out of service since 17 December due to generator lower guide bearing failure.
1.3.9 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.10 Unit 10 was out of service from 1151 until 1214 on 02 February for 3D cam testing.

1.3.11 Unit 11 has remained out of service since 12 June due to rotor damage.
1.3.12 Unit 13 was out of service from 0930 until 1148 on 06 February to facilitate the Behavioral Guidance Structure (BGS) repairs.

1.3.13 Unit 14 was out of service from 0937 until 1135 on 06 February to facilitate the BGS repairs.

1.3.14 Unit 16 was out of service from 0930 until 1148 on 06 February to facilitate the BGS repairs.

1.3.15 Unit 17 was out of service from 0940 until 1131 on 06 February to facilitate the BGS repairs.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 and F2 remain out of service while the WS fishway is dewatered.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV1-1 was closed for cleaning from 0959 until 1324 on 02 February; from 1523 until 1551 on 04 February; and from 1453 until 1545 on 07 February.
2.1.2 FV5-3, FV5-4, FV5-9 and FV6-9 remain closed while Cascades Island and WS remain dewatered.
2.2 STS/VBS inspections.  No STS/VBS activities occurred this reporting week.  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1, 3
	NA
	NA
	Removed until 15 September.

	11-18
	NA
	NA
	Six STSs have broken gearboxes due to freezing in December.


2.3 Dewatering and Fish Salvage.  The following fish salvage and dewatering activities occurred this week:
2.3.1 On 3 February Fisheries removed 30 sturgeon from the south monolith.  All fish were released to the PH2 tailrace.
2.3.2 On 4 February Fisheries removed eight sturgeon from the PH2 collection channel AWS conduit.  Five sturgeon were in good condition, three were stuck on the drain valve, one will likely die.
3 RESEARCH  
3.1 WDFW Fish Counting.  Video counting at Bradford Island continues.
3.2 WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.
4 FISHWAYS 

4.1 Project biologists inspected 1-2, 5 February.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND 

	2/2, 2/5
	B-Branch 
	Incorrect diffuser positions
	System in manual
	Operators adjusted.
	

	CASCADES ISLAND- OOS for winter maintenance

	WASHINGTON SHORE- OOS for winter maintenance

	DSM1/ITS – DSM1 is OOS until early September

	DSM2/ JMF – OOS for winter maintenance


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 05 February.  B-branch PLC remains in manual.
4.5.2 WG 2 remains in manual due to an inability to raise >10.9’.  
4.5.3 Cascades Island remains dewatered. 
4.5.4 WS fishway remains dewatered.  
4.5.5 The AFF remains dewatered. 
4.5.6 All Bradford Island SLEDs were installed by 30 January. 
4.6 Juvenile Fishways.

4.6.1 DSM1 remains dewatered.
4.6.2 DSM2 remains dewatered. 
4.6.3 PH1 ITS was closed from 1500 until 1832 on 06 February due to a non-reportable oil sheen in the forebay of PH1.
4.7 Lamprey Fishways.  BI and WS AWS lamprey ramps remain winterized.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation in FY09.  Wall removal in FY10.
5.2 TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A 06 November teletype set the BON upper forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.  

7.2 A 31 December teletype, regarding BON tailwater operations for chum egg incubation, requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 1 January 2009 until further notice. 
7.3 A 02 February teletype (modified on 05 and 06 February) requested limited generation of 45 kcfs, soft constraint, and 50 kcfs, hard constraint, from 1000 until 1400 on 06 February at PH2.  This request is to facilitate the repairs needed to the BGS.  To maintain chum flows the Project may operate outside the 1% turbine efficiency, and as a last resort, may implement spill.
JAMES R. MAHAR, P.E.

Operations Manager
1

