CENWP-OD-B                                                                                                                                  15 February 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 7 of 2009, which covers the period from 08 through 14 February 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 119.9 to 168.2 kcfs.  Daily average project tailwater ranged from 11.6’ to 14.7’ msl.  Daily average powerhouse forebay elevation ranged from 73.2’ to 75.6’ msl.  Daily average river temperature ranged from 37 ºF to 38ºF.  Secchi disk measurements were between 5.0’ to 7.0’.
1.2 Spill Bay 18, which provides attraction flow for B-Branch, is open 6” during daylight hours.  Daily average spill was 0.6 kcfs. 
1.3 Unit Operation.  Powerhouse 1 remains the priority powerhouse.
1.3.1 Unit 1 was out of service from 0714 until 0728 on 08 February for governor low pressure alarm testing.
1.3.2 Unit 4 was out of service from 1214 until 1446 on 11 February to facilitate packing tightening.

1.3.3 Unit 5 was out of service from 0944 until 1126 on 10 February for bank 7/8 switching.

1.3.4 Unit 6 was out of service from 0944 until 1126 on 10 February for bank 7/8 switching.

1.3.5 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.6 Unit 8 has remained out of service since 17 December due to generator lower guide bearing failure.
1.3.7 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.8 Unit 11 has remained out of service since 12 June due to rotor damage.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 and F2 remain out of service while the WS fishway is dewatered.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV1-1 was closed for cleaning from 0657 until 0716 on 09 February and from 0835 until 1034 on 12 February.
2.1.2 FV5-3, FV5-4, FV5-9 and FV6-9 remain closed while Cascades Island and WS remain dewatered.
2.2 STS/VBS inspections.  No STS/VBS activities occurred this reporting week.  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1, 3
	NA
	NA
	Removed until 15 September.

	11-18
	NA
	NA
	Six STSs have broken gearboxes due to freezing in December.


2.3 Dewatering and Fish Salvage.  The following fish salvage and dewatering activities occurred this week:
2.3.1 On 11 February Fisheries removed about 100 juvenile lamprey, two bluegill, five stickleback, one pumpkinseed, and one crappie from U12 and U14 gatewells, during debarking activities.  All fish were released to the tailrace.  
3 RESEARCH  
3.1 WDFW Fish Counting.  Video counting at Bradford Island continues.
3.2 WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.
4 FISHWAYS 

4.1 Project biologists inspected 9, 11-13 February.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND 

	2/9, 2/11, 2/13
	A-branch weir
	Reading >1.0’
	Unknown
	No action taken.
	

	2/12-13
	B-Branch
	FG3-25 incorrect position for TW
	System in manual.
	Operators adjusted.
	

	CASCADES ISLAND- OOS for winter maintenance

	WASHINGTON SHORE- OOS for winter maintenance

	DSM1/ITS – DSM1 is OOS until early September

	DSM2/ JMF – OOS for winter maintenance


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 13 February.  B-branch PLC remains in manual.
4.5.2 WG 2 remains in manual due to an inability to raise >10.9’.  
4.5.3 Cascades Island remains dewatered. 
4.5.4 WS fishway remains dewatered.  The AWS and south monolith remain dewatered completely.  The north monolith will be fully dewatered on 17 February.
4.5.5 The AFF remains dewatered. 
4.6 Juvenile Fishways.

4.6.1 DSM1 remains dewatered.
4.6.2 DSM2 remains dewatered. 
4.7 Lamprey Fishways.  BI and WS AWS lamprey ramps remain winterized.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation in FY09.  Wall removal in FY10.
5.2 TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A 06 November teletype set the BON upper forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.  

7.2 A 31 December teletype, regarding BON tailwater operations for chum egg incubation, requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 1 January 2009 until further notice. 
JAMES R. MAHAR, P.E.

Operations Manager
1

