CENWP-OD-B                                                                                                                                  24 February 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 8 of 2009, which covers the period from 15 through 21 February 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 126.3 to 131.1 kcfs.  Daily average project tailwater was 11.6’ msl.  Daily average powerhouse forebay elevation ranged from 73.9’ to 74.8’ msl.  Daily average river temperature ranged from 37 ºF to 38ºF.  Secchi disk measurements were 7.0’.
1.2 Spill Bay 18, which provides attraction flow for B-Branch, is open 6” during daylight hours.  Daily average spill ranged from 0.6-0.7 kcfs.
1.3 Unit Operation.  Powerhouse 1 remains the priority powerhouse.
1.3.1 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.2 Unit 8 has remained out of service since 17 December due to generator lower guide bearing failure.
1.3.3 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.4 Unit 11 has remained out of service since 12 June due to rotor damage.
1.3.5 Unit 17 was out of service from 0928 until 1114 on 18 February for HC pump replacement.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 and F2 remain out of service while the WS fishway is dewatered.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV1-1 was closed for cleaning from 1505 until 1716 on 17 February and from 1358 until 1419 on 21 February.
2.1.2 FV5-3, FV5-4, FV5-9 and FV6-9 remain closed while Cascades Island and WS remain dewatered.
2.2 STS/VBS inspections.  No STS/VBS activities occurred this reporting week.  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1, 3
	NA
	NA
	Removed until 15 September.

	11-18
	NA
	NA
	Six STSs have broken gearboxes due to freezing in December.


2.3 Dewatering and Fish Salvage.  The following fish salvage and dewatering activities occurred this week:
2.3.1 On 17 and 18 February Fisheries removed one lamprey ammocoete, two sturgeon, and two suckers from the north monolith.  All fish were released to the tailrace.  
2.3.2 On 18 February Fisheries removed four sturgeon, four juvenile chinook, one adult lamprey, 29 sculpin, 10 suckers, one bass, six stickleback , one longnose dace, and one crawdad from north section of the PH2 AWS conduit.  All fish were released to the tailrace.
3 RESEARCH  
3.1 WDFW Fish Counting.  Video counting at Bradford Island continues.
3.2 WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.
4 FISHWAYS 

4.1 Project biologists inspected 15, 17, and 19 February.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.

	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND 

	2/17, 19
	B-Branch
	FG3-26 incorrect position for TW
	System in manual.
	Operators adjusted.
	

	CASCADES ISLAND- OOS for winter maintenance

	WASHINGTON SHORE- OOS for winter maintenance

	DSM1/ITS – DSM1 is OOS until early September

	DSM2/ JMF – OOS for winter maintenance


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 19 February.  B-branch PLC remains in manual.
4.5.2 WG 2 remains in manual due to an inability to raise >10.9’.  
4.5.3 Cascades Island remains dewatered. 
4.5.4 WS fishway remains dewatered.  The north monolith was fully dewatered on 17 February (See 2.3.1 and 2.3.2).  The south and north monolith returned to tailwater with SLEDs installed on 19 February.
4.5.5 The AFF remains dewatered. 
4.6 Juvenile Fishways.

4.6.1 DSM1 remains dewatered.
4.6.2 DSM2 remains dewatered.   It is scheduled to be watered up on 24 February.
4.6.3 PH1 ITS was dewatered and bulkheads installed on 17 February for automated gate installation.
4.7 Lamprey Fishways.  BI and WS AWS lamprey ramps remain winterized.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation began on 17 February (see 4.6.3).  Wall removal in FY10.
5.2 TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.
6 HAZMAT, SPILLS AND CLEANUP.   
6.1 At 1338 on 19 February, it was reported the gearbox on the STS in Unit 17C had failed and was leaking oil.  The oil was contained in the 17C gatewell, absorbents were placed in the gateslot, and the STS was moved over an OOS unit.  The orifices have been closed since 18 December for winter maintenance.  It is estimated that less than 5 gallons of oil leaked into the gatewell.  No oil was released into the river; all oil was contained in 17C gatewell. 
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A 06 November teletype set the BON upper forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.  

7.2 A 31 December teletype, regarding BON tailwater operations for chum egg incubation, requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 1 January 2009 until further notice. 

JAMES R. MAHAR, P.E.

Operations Manager
1

