CENWP-OD-B                                                                                                                                  09 March 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 10 of 2009, which covers the period from 01 through 07 March 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 114.2 to 157.8 kcfs.  Daily average project tailwater ranged from 11.6’ to 14.2’ msl.  Daily average powerhouse forebay elevation ranged from 75.1’ to 76.1’ msl.  Daily average river temperature ranged from 39 - 40ºF.  Secchi disk measurements ranged from 5.0’ to 6.5’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-Branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.2 to 1.4 kcfs.
1.3 Unit Operation.  Powerhouse 1 remains the priority powerhouse until 01 March.
1.3.1 Unit 6 was out of service from 2100 on 05 March until 1612 on 06 March due to current transformer replacement. 

1.3.2 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.3 Unit 8 has remained out of service since 17 December due to generator lower guide bearing failure.
1.3.4 Unit 9 has remained out of service since 04 August for turbine rehab.
1.3.5 Unit 11 has remained out of service since 12 June due to rotor damage.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F2 returned to service at 0855 on 04 March.  It had been out of service since 10 January for annual maintenance and WA shore ladder outage.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV1-1 was closed for cleaning from 0759 until 1415 on 02 March and from 0821 until 0855 on 03 March. 
2.1.2 FV5-9 was closed for cleaning from 1500 until 1545 on 05 March.
2.2 STS/VBS inspections.  The following STS/VBS activities occurred this reporting week.  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1, 3
	NA
	NA
	Removed until 15 September.

	11
	NA
	NA
	U11 remains OOS

	12-18
	NA
	
	STSs installed.


2.3 Dewatering and Fish Salvage.  No fish salvage and dewatering activities occurred this week.
3 RESEARCH  
3.1 PSMFC.  Juvenile fish condition and index monitoring at the Smolt Monitoring Facility (SMF) began at 0700 on 02 March.  

3.2 WDFW Fish Counting.  Video counting at Bradford Island continues.

3.3 WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.
3.4 USDA Wildlife Services. Hazing from shore began on 02 March.
4 FISHWAYS 

4.1 Project biologists inspected 01-07 March.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND 

	3/1-3/3
	BI
	No temps taken
	Probe not installed
	
	

	3/1-3/3, 3/5
	A-branch weir
	Reading <1.0’>
	Unknown
	No action taken.
	

	3/3, 3/5, 3/6
	B-branch diff.
	Incorrect position
	System in manual
	Operators adjusted.
	

	3/3
	B-branch entrance
	Diff. >2.0’
	System in manual
	Operators adjusted.
	

	3/7
	FG 3-25
	Incorrect position
	System in manual
	Operators adjusted
	

	CASCADES ISLAND

	3/4
	FG 6-14
	Closed
	PLC issues
	PLC reset
	

	3/4
	South gate
	Closed
	PLC issues
	PLC reset
	

	3/4
	CI entrance
	Diff. <1.0’
	PLC issues
	PLC reset
	

	3/7
	UMT staff gage
	>1.0
	Unknown
	Operators adjusted
	

	WASHINGTON SHORE

	3/1
	Weir 37 
	Staff gauge gone
	Moved for new AFF picket leads.
	Riggers to re-install next week.
	

	3/1-3/4
	F2
	OOS
	Maintenance
	In service on 3/4
	

	3/3
	PH2 entrances
	Diff. <1.0’
	F1 on standby to pull F2 tail logs
	F1 back in service by 1100.
	

	DSM1/ITS – DSM1 is OOS until early September

	3/1
	ITS
	Not in service
	Contractors delayed
	Watered up on 3/2
	

	3/6
	ITS
	S. gate closed
	Facilitate dive
	Opened upon completion
	

	DSM2/ JMF

	3/1
	11A-N, 11C-S
	Closed
	11A-N has air leak.  11C-N jammed.
	TR’d
	09-119557

	3/1
	13A-N
	Orifice light off
	Bad light fixture
	TR’d
	09-119562


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

 average

	3/1
	38.1
	NA

	3/2
	38.0
	NA

	3/3
	38.4
	NA

	3/4
	38.5
	38.3

	3/5
	39.0
	38.7

	3/6
	39.0
	38.8

	3/7
	39.1
	38.9


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  

4.5 Adult Fishways. 
4.5.1 Calibration was checked on 06 March.  B-branch PLC remains in manual.  Cascades Island PLC is functioning in auto.
4.5.2 WG 2 remains in manual due to an inability to raise >10.9’.  
4.5.3 Cascades Island returned to service at 1500 on 28 February.  All SLEDs were installed by 1534 on 27 February.
4.5.4 WS fishway returned to service at 1040 on 28 February.
4.5.5 Installation of the FOG sea lion exclusion bars was completed on 04 March.  11 FOGs are in service, one remains out of service until structural repairs can be made.  
4.5.6 On 02 March, the NUE was closed, and the SDE, SUE, and NDE were open approximately 8’.  This was necessary to achieve an entrance differential of 1.0’ until F2 returned to service on 04 March.  
4.5.7 The AFF remains dewatered. 
4.6 Juvenile Fishways.

4.6.1 DSM1 remains dewatered.
4.6.2 DSM2 returned to service on 24 February.  Hydro-cannons were turned on 26 February.
4.6.3 SMF switch-gate was placed in sample mode at 0630 on 02 March.
4.6.4 PH1 Ice and Trash Sluiceway was watered up on 02 March.  Chain gates 3B, 6C, and 10B are open.
4.6.5 B2CC was open from 0830 until 1155 on 04 March to flush debris in PH2 forebay.  
4.6.6 PH1 ITS was closed from 0710 until 1235 on 06 March to facilitate monolith repair.
4.7 Lamprey Fishways.  BI and WS AWS lamprey ramps remain winterized.
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Gate installation continues.  Wall removal in FY10.
5.2 TIE crane.  The TIE crane boom repair has been delayed.
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A 06 November teletype set the BON upper forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.  

7.2 A 31 December teletype, regarding BON tailwater operations for chum egg incubation, requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 01 January 2009 until further notice. 
7.3 A 26 February teletype requests that Unit 6 be placed as last on/first off in the unit priority list.  This is to accommodate the alignment measurement and testing of Unit 7.  Unit 6 will return to normal FPP unit priority when the Unit 7 work has been completed or at 0001 on 13 March, whichever comes first.

7.4 A 03 March teletype states that the Bonneville Dam Corner Collector will be opened to pass debris from approximately 0700-1200 hrs, Wednesday, 04 March. 
JAMES R. MAHAR, P.E.

Operations Manager
1

