
CENWP-OD-B























19 July 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 29 of 2009, which covers the period from 12 through 18 July 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 147.7 to 189.1 kcfs.  Daily average project tailwater ranged from 13.3’ to 15.5’ msl.  Daily average powerhouse forebay elevation ranged from 75.0’ to 76.1’ msl.  Daily average river temperature was 68ºF.  Secchi disk measurements ranged from 3.0’ to 6.0’.
1.2 Daily average spill ranged from 95.8 to 101.0 kcfs.
1.2.1 Spillbay 17 remains on two dogs (2.9’).  The bay should be at 3.5’ but due to a broken hoist it has to be dogged instead.  Flow is compensated through adjacent bays.
1.3 Unit Operation.  Powerhouse 2 remains the priority powerhouse.
1.3.1 Unit 0 was out of service from 1432 until 1743 on 15 July for electrical PMs on the breaker.

1.3.2 Unit 5 was out of service from 0825 until 1853 on 15 July due to BPA switchyard work.

1.3.3 Unit 6 went out of service at 0826 on 13 July for a five year overhaul.

1.3.4 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.5 Unit 8 was out of service from 0825 until 1846 on 15 July due to BPA switchyard work 

1.3.6 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.7 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.8 Unit 12 was out of service from 0430 until 1142 on 14 July to facilitate the repair of an oil leak.  No oil entered the river.
1.3.9 Unit 16 has remained out of service since 09 May due to exciter troubles and a grounding issue.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  No AWS valves were closed this reporting week:
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week:  
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1-2
	NA
	NA
	Remains out of service until 03 September.

	11, 16
	NA
	NA
	Out of service

	12-15, 17-18
	NA
	NA
	


2.2.1 Dewatering and Fish Salvage.  The following fish salvage/ dewatering activity occurred this week:
2.2.1.1 On 14 July, Fisheries removed one lamprey from the draft tube of Unit 6 

3 RESEARCH  

3.1 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues. 
3.2 CRITFC- JMF video.  Waiting on new equipment for monitoring juvenile fish passage.  
3.3 CTUIR.  Radio-tagging collections completed.  Total of 50 lamprey collected for 2009.  

3.4 NOAA-FGE.  Test releases of PIT-tagged run of the river fish concluded on 13 July.  Unit 14 orifices returned to auto at 1203 on 13 July.
3.5 NOAA Lamprey.  Trapping lamprey at the AFF for passage evaluations.  On 16 July, NOAA reported two lamprey mortalities in the NDE lamprey trap.  They were given to U of I for proximate analysis.  
3.6 NOAA- pathogens. Determination of pathogen prevalence in juvenile salmonids.  25 sub-yearling chinook were collected at the JMF.
3.7 NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6. 

3.8 PNNL- BGS.  All hydrophones are installed and collecting data for the BGS evaluation.  
3.9 PSMFC- Smolt monitoring.  Daily condition and index monitoring continues.  Fallbacks recorded crossing the separator bars included; one salmon.  Gas Bubble Trauma (GBT) exams occur twice a week; see www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  25 sub-yearling chinook were collected for pathogen testing.
3.10 WDFW Fish Counting.  Visual counting continues at Bradford Island and Washington Shore fishways. Nighttime video counts began 15 June.
3.11 USDA Wildlife Services. Avian hazing continues.

3.12 University of Idaho.  Tagging lamprey for evaluation of the Cascades Is. entrance weir.
4 FISHWAYS 

4.1 Project biologists inspected 12 through 18 July.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) --Nothing to report

	CASCADES ISLAND (CI)--Nothing to report

	WASHINGTON SHORE (WS) 

	7/12-13, 15-16
	Entrances
	<13.0’ opening
	In manual
	Operators adjusted.
	

	7/12
	Weir 38
	Reading < 1.0’
	Unknown
	Operators adjusted.
	


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.2.3 CI south entrance gate remains broken and closed.  It is been OOS since 10 April.  It will remain in the closed position for all tailwater elevations during the modified entrance evaluation. 
4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington Shore.  

4.3.1 The WS and BI probes have been sent to the manufacturer to be calibrated.  Probes are scheduled for installation the week of 19 July. The AFF probe is being used as a surrogate.
Table 3.  Bonneville Fishway Temperatures

	Date
	AFF average

	7/12
	66.2

	7/13
	65.9

	7/14
	66.1

	7/15
	66.2

	7/16
	66.8

	7/17
	67.8

	7/18
	68.4


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 17 July.
4.5.2 The Washington Shore fishway entrances are in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening.

4.5.3 There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  The last gate was removed for maintenance and replaced with a bulkhead.
4.6 Juvenile Fishways.
4.6.1 To provide the best flow possible until the new gates can be automated, the PH1 ITS chaingates were set as follows:  1B- 71’msl, 3B- 72’ msl, 6C- 72’msl, and 9A- 72’.  Fisheries will monitor forebay elevations and adjust gates 3B and 6C to maintain >2.5’ depth.
4.6.2 The PH1 ITS was closed from 0727 until 1429 on 14 July.
4.7 Lamprey Fishways.  
4.7.1 The CI entrance weir and bulkhead slot filler are installed.  
4.7.2 All lamprey passage structures remain watered-up.   
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Wall removal is scheduled for FY10.  Old DSM bypass equipment in the tailrace is scheduled for removal in FY10 as well.
5.1.1 The Program Logic Control (PLC) for the automated gates has not been completed.
5.1.2 The keeper pin for gate 3B was repaired on 14 July.
5.2 TIE crane.  The new boom is to arrive in late July.
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 17 May and revised on 18 May provides guidance for voluntary and involuntary spill by project as well as spill caps per project for various total dissolved gas (TDG) levels.

7.2 A teletype sent on 19 June requests the summer spill operations starting at 0001 on 21 June.  From 21 June until 2400 on 20 July, the Project will spill approximately 85 kcfs during daytime hours and to the 120% gas cap at night.  From 0001 on 21 July until 2400 on 31 August, the Project will spill approximately 75 kcfs during the day and up to the 120% gas cap at night.

7.3 A teletyple sent on 13 July requests that from 0900 to 1500 on 17 and 18 July, the forebay elevations be maintained at 75.0’-76.5’ msl as a hard constraint and 75.5’-76.5’ as a soft constraint.  This operation is requested to assist the Gorge Games outrigger race.

7.4 A teletype sent on 14 July requests that from 0600 on 15 July until 1800 on 17 July, the forebay elevation be maintained at 75.0’ – 76.5’ msl. as a hard constraint and 75.5’ – 76.5’ msl. as a soft constraint.  This operation is requested to reduce debris in tribal fishing nets, reduce entanglement of fishing nets, minimize boat access problem, and reduce the chances of nets being torn from their anchors by limiting pool fluctuation.
7.5 A teletype sent on 16 July changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July until U11 returns to service.
7.6 Starting on 20 July, Ben Hausmann will begin a 120-day detail in the NWP Planning Section and Jon Rerecich will begin a 120-day detail as Lead Project Biologist at Bonneville.

JAMES R. MAHAR, P.E.

Operations Manager
Page 1 of 3
1
Page 3 of 3

