CENWP-OD-B























30 August 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 35 of 2009, which covers the period from 23 through 29 August 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 103.6 to 123.2 kcfs.  Daily average project tailwater ranged from 9.9’ to 11.6’ msl.  Daily average powerhouse forebay elevation ranged from 74.4’ to 76.2’ msl.  Daily average river temperature ranged from 70ºF to 71ºF.  Secchi disk measurements ranged from 5.0’ to 7.0’.
1.2 Daily average spill ranged from 60.7 to 79.9 kcfs.
1.2.1 Spillbay 17 remains on two dogs (2.9’).  It will be closed on 31 August during business hours and flow will be made up through adjacent bays.  
1.2.2 All spillbays will be closed at 2400 on 31 August except for bays 1 and 18 which will be open 0.5 ft. for attraction flow to the ladder entrances.  
1.3 Unit Operation.  Powerhouse Two remains the priority powerhouse.
1.3.1 Unit 2 was out of service from 0039 on 24 August until 1502 on 26 August for replacement of a cooling water pump.

1.3.2 Unit 6 has remained out of service since 13 July for a five year overhaul.

1.3.3 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.4 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.5 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.6 Unit 16 has remained out of service since 09 May due to exciter troubles and a grounding issue.

1.3.7 Unit 18 was out of service from 0112 on 24 August until 1620 on 25 August for annual maintenance.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 was on standby for lamprey testing from: 2206 on 28 August until 0413 on 29 August.

1.4.2 F2 was on standby for lamprey testing from: 2200 on 23 August until 0354 on 24 August; 2155 on 24 August until 0411 on 25 August; 2153 on 27 August until 0404 on 28 August.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following  AWS valves were closed this reporting week: 

2.1.1 FV1-1 was closed for cleaning from: 1520 until 1540 on 27 August.

2.1.2 FV3-9 was closed for cleaning from: 1409 until 1420 on 24 August; 1519 until 1525 on 27 August.
2.1.3 FV5-9 was closed for cleaning from: 1526 until 1545 on 24 August; 1520 until 1540 on 27 August.
2.1.4 FV6-9 was closed for cleaning from: 1526 until 1545 on 24 August; 1520 until 1540 on 27 August.

2.2 STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1-2
	NA
	NA
	Remains out of service until 01 September.

	11
	NA
	NA
	Out of service

	12
	8/24
	645
	A-slot VBS cleaned on 27 August

	13
	8/24
	84
	

	14
	8/24
	127
	

	15
	8/24
	245
	

	16
	NA
	NA
	Out of service

	17
	8/24
	139
	

	18
	8/24
	664
	.


2.2.1 Dewatering and Fish Salvage.  No fish salvage or dewatering activities occurred this week.
3 RESEARCH  

3.1 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  Daily average temperatures dropped below 69.5ºF on 25 August, and normal trapping operations resumed. 
3.2 CRITFC- JMF video.  New video equipment installed for monitoring juvenile fish passage.  
3.3 NOAA Lamprey.  Trapping lamprey at the AFF for passage evaluations continues. 
3.4 NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6. 

3.5 NWW truck release site.  Trucking and release at BON began on 16 August.

3.6 PSMFC- Smolt monitoring.  Modified sampling protocols due to elevated river temperature occurred 23-25 August.  Daily average temperature dropped below 69.5 ºF on 25 August.  No fallbacks were recorded crossing the separator bars.  Gas Bubble Trauma (GBT) exams occur twice a week; see www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  No fish were held for researchers this week.    
3.7 WDFW Fish Counting.  Visual counting continues at Bradford Island and Washington Shore fishways. Nighttime video counts began 15 June.
3.8 WDFW Tule counts.  Tule counting began on 16 August.

3.9 USGS Shad.  Collecting juvenile shad from the Juvenile Fish Monitoring Facility for ongoing research on impacts of American Shad on the Columbia River.  No shad collected this week.
3.10 University of Idaho.  Tagging lamprey for evaluation of the Cascades Is. entrance weir concluded.
4 FISHWAYS 

4.1 Project biologists inspected 23 through 29 August.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) nothing to report

	
	
	
	
	
	

	CASCADES ISLAND (CI) 

	8/23
	CI diffusers
	FG6-11 open
	FV5-4 pressure
	Ops closed.
	

	8/23-24
8/25-29
	CI diffusers
	FG6-18 open
	FV5-4 conduit pressure
	Fisheries closed on 8/24.
	

	WASHINGTON SHORE (WS) 

	8/23
	Weir 38
	Reading < 1.0’
	Unknown
	Adjusted valve 11
	

	PH1 ITS 

	8/23
	Chaingates
	Open < 2.5’
	In manual
	No action taken
	


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.3 Fishway Temperatures.  All four temperature probes are experiencing technical difficulties.  Please see the following website for Bonneville temperatures:  http://www.nwd-wc.usace.army.mil/tmt/documents/ops/temp/200908.lcol.html
Table 3.  Bonneville Fishway Temperatures

	Date
	WS Avg
	BI Avg
	AFF Avg
	JMF Avg

	8/23
	NA
	NA
	NA
	NA

	8/24
	NA
	NA
	NA
	NA

	8/25
	NA
	NA
	NA
	NA

	8/26
	NA
	NA
	NA
	NA

	8/27
	NA
	NA
	NA
	NA

	8/28
	NA
	NA
	NA
	NA

	8/29
	NA
	NA
	NA
	NA


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 28 August.
4.5.2 The Washington Shore fishway entrances are in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.
4.5.3 There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  One gate was removed for maintenance and replaced with a bulkhead.
4.5.4 The BI exit was closed for cleaning from: 1409 until 1420 on 24 August; 0910 until 0930 on 26 August; 1345 until 1357 on 26 August; 1519 until 1525 on 27 August.  

4.5.5 FV4-3 in manual since 25 August.

4.5.6 CI south entrance gate was repaired the week of 16 August.  It will remain in the closed position for all tailwater elevations during the modified entrance evaluation.

4.6 Juvenile Fishways.
4.6.1 To provide the best flow possible, until the new gates can be automated, the PH1 ITS chaingates were set as follows:  1B- 72’msl and 9A- 72’.  The Project will monitor forebay elevations and adjust gates 3B and 6C to maintain >2.5’ depth.
4.6.2 The B2CC is scheduled to close on the afternoon of 31 August.
4.7 Lamprey Fishways.  
4.7.1 The CI entrance weir and bulkhead slot filler are installed.  
4.7.2 All lamprey passage structures remain watered-up. 
5 CONSTRUCTION
5.1 PH1 Ice and Trash Sluiceway Wall Removal.  Wall and DSM1 outfall scheduled for removal in FY10.
5.1.1 The Program Logic Control (PLC) for the automated gates has not been completed.
5.2 TIE crane.  The crane is scheduled to be available by the 2010 fish passage season.
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 13 August requests BON spill 75 kcfs during daytime hours and spill up to the 120% TDG cap during nighttime hours, using the spill pattern in Table BON-14 of the 2009 FPP.  This action is effective from 13 August until 2400 on 31 August.

7.2 A teletype sent on 16 July changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July until U11 returns to service.
7.3 A teletype sent on 27 July changes the unit operation for PH2.  PH2 units will operate at the low end to mid point of the 1% efficiency range.

7.4 A teletype sent on 21 August requests the forebay be operated at 75.0 – 76.5’ msl as a hard constraint and 75.5’ – 76.5’ msl as a soft constraint from 0600 on 24 August until 1800 on 27 August.  This action is to limit pool fluctuation, during tribal fishing, to: reduce local currents that sweep debris into tribal fishing nets; reduce rapid water level changes that entangle nets; minimize boat access problems; avoid tearing nets from their anchors.  A teletype sent on 28 August extends this request to include from 0600 on 31 August until 1800 on 04 September.  
7.5 Teletype sent on 28 August requests outflows from BON and TDA do not exceed 150 kcfs and remain as low and constant as possible from 0700 until 1130 on 07 September.  This request is to reduce river currents during the cross channel swim at Hood River.

JERRY CARROLL
Acting Operations Manager
Page 1 of 3
1
Page 2 of 3

