CENWP-OD-B






















22 November 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 47 of 2009, which covers the period from 15 through 21 November 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 110.9 to 130.6 kcfs.  Daily average project tailwater ranged from 11.5’ to 12.4’ msl.  Daily average powerhouse forebay elevation ranged from 76.4’ to 77.2’ msl.  Daily average river temperature ranged between 50ºF to 52ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill was 1.2 kcfs.  

1.3 Unit Operation.  Powerhouse Two is the priority powerhouse.
1.3.1 Unit 3 was out of service from 0800 until 1429 and from 1449 until 1504 on 17 November for BPA relay testing.  Unit 3 went out of service at 1703 on 19 November due to a loss of Bank 3/4.

1.3.2 Unit 4 was out of service from 0800 until 1447 and from 1449 until 1504 on 17 November for BPA relay testing.  Unit 4 went out of service at 1703 on 19 November due to a loss of Bank 3/4.

1.3.3 Unit 5 was out of service from 0800 until 1659 on 18 November for BPA relay testing.
1.3.4 Unit 6 was out of service from 0800 until 1659 on 18 November for BPA relay testing.  Unit 6 went out of service at 0905 on 21 November for DSM1 orifice removal.

1.3.5 Unit 8 was out of service from 0800 until 1659 on 18 November for BPA relay testing.

1.3.6 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.7 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.8 Unit 10 went out of service at 0726 on 16 November for DSM1 orifice removal.
1.3.9 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.10 Unit 17 has remained out of service since 05 October for a four year overhaul.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed for cleaning this reporting week: 

2.1.1 FV1-1- Closed for cleaning from 1335 until 1350 on 16 November.
2.1.2 FV3-9- Closed for cleaning from 1613 until 1630 on 16 November. 
2.1.3 FV5-9- Closed for cleaning from 1100 until 1126 on 16 November.

2.1.4 FV6-9- Closed for cleaning from 1148 until 1200 on 16 November.

2.2 STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  Report 0944 listed the incorrect date of inspections.
	Unit
	Date
	Run Hours
	Comments

	1, 2
	NA
	
	STSs and VBSs removed

	11, 16
	NA
	
	Out of service

	12-15, 17-18
	NA
	NA
	Inspections scheduled for 23 -25 November.


2.2.1 Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.
3 RESEARCH  

3.1 NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6. 

3.2 ODFW/WDFW sea lions.  Moved the forebay sea lion trap on 19 November.
3.3 Smith-Root sea lion array.  Array installation scheduled for 02 December in the upstream migration channel from Cascades Is. to Powerhouse 2.
3.4 WDFW Fish Counting.  Video counting at Bradford Island and Washington Shore continues.
4 FISHWAYS 

4.1 Project biologists inspected 15 through 21 November 
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	11/15-16
	PH1 S entrance
	Differential < 1.0’
	Unknown
	Ops adjusted.
	

	11/20
	BI Weir
	Reading <1.0’>
	Unknown
	Self corrected
	

	CASCADES ISLAND (CI)- nothing to report

	
	
	
	
	
	

	WASHINGTON SHORE (WS)- nothing to report

	
	
	
	
	
	


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder.  

4.3.1 Three out of four temperature probes are experiencing technical difficulties.
Table 3.  Bonneville Fishway Temperatures

	Date
	WS Avg
	BI Avg

	11/15
	NA
	51.0

	11/16
	NA
	50.8

	11/17
	NA
	50.5

	11/18
	NA
	50.1

	11/19
	NA
	50.2

	11/20
	NA
	50.0

	11/21
	NA
	49.7


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 20 November.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  

4.5.3 There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  One gate was removed for maintenance and replaced with a bulkhead.
4.5.4 FV4-3 remains in manual due to a defective conduit sensor.  Repairs scheduled for 09/10.
4.5.5 FV5-3 and FV5-4 were returned to auto on 17 November, after the tailwater sensors were calibrated. 
4.5.6 The PH1 ice and trash sluiceway (ITS) remains dewatered.
4.6 Juvenile Fishways.
4.6.1 The B2CC remains closed.
4.6.2 DSM1 wall and orifice removal continues.
4.7 Lamprey Fishways.  
4.7.1 The Cascades Is. entrance weir remains installed.  
4.7.2 All lamprey passage structures (LPSs) have been dewatered. 
4.7.3 The PH2 NDE ramp remains in the lowered position.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  Crane rails replacement continues.  New crane in FY11.  
5.2 PH1 Ice and Trash Sluiceway Wall Removal.  Wall and DSM1 outfall removal continues.
5.3 TIE crane.  The boom was delivered on 16 November.  
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010 to support chum spawning below the dam.  
7.3 A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.
7.4 A teletype sent on 05 November requests BON tailwater elevation hard constraint of no less than 11.3’ msl during all hours and a soft constraint of 11.3’ to 11.7’, with a target of 11.5’, from 0600 until 1700 daily.  This is effective from 0600 on 06 November until further notice.  This request is to provide necessary flows for chum spawning.  
JERRY CARROLL
Acting Operations Manager
Page 1 of 3
1
Page 3 of 3

