[image: image1.wmf][image: image2.wmf][image: image3.wmf]

CENWP-OD-B






















14 December 2009
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 50 of 2009, which covers the period from 06 through 12 December 2009.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 135.0 to 149.1 kcfs.  Daily average project tailwater ranged from 12.6’ to 13.1’ msl.  Daily average powerhouse forebay elevation ranged from 75.7’ to 76.0’ msl.  Daily average river temperature ranged between 42ºF to 45ºF.  Secchi disk measurements ranged from 5.0’ to 7.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 0.5 to 3.4 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse.
1.3.1 Unit 3 returned to service, after being out since 19 November, at 1053 on 08 December.
1.3.2 Unit 4 returned to service, after being out since 19 November, at 1053 on 08 December.

1.3.3 Unit 5 has remained out of service since 04 December due to DSM1 orifice removal.
1.3.4 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.5 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.6 Unit 10 returned to service, after being out since 16 November, at 0900 on 21 November.  Unit 10 was out of service from 0358 until 1636 on 08 December for thrust cooler cleaning.
1.3.7 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 remains out of service for annual maintenance.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week: 

2.1.1 FV1-1, 3-7, 3-9, 4-3, and 4-4 remain closed for winter maintenance in Bradford Island.
2.1.2 FV5-9- closed for cleaning from 1054 until 1100 on 07 December.
2.1.3 FV6-9-closed for cleaning from 1100 until 1110 on 07 December.

2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	1, 2
	NA
	
	STSs and VBSs removed

	11
	NA
	
	Out of service

	12-13, 15
	NA
	
	Scheduled to be pulled on 15 December.

	14
	12/7
	
	Scheduled to be pulled on 15 December.

B and C slot VBSs cleaned on 09 December.

	16
	12/8
	
	Scheduled to be pulled on 15 December.

VBSs cleaned on 08 December.

	17
	NA
	
	Out of service

	18
	12/7
	
	Scheduled to be pulled on 15 December.
VBSs cleaned on 07, 08, and 09 December.


2.3 Dewatering and Fish Salvage.  The following dewatering/fish salvage activities occurred this week:
2.3.1.1 On 07 December USACE Fisheries, with the much appreciated assistance from USFWS, CRITFC, NOAA, BPA, and PSMFC, removed from the Bradford Island ladder one unclipped adult steelhead, 13 clipped adult steelhead, 10 juvenile steelhead, 11 sturgeon, six lamprey, two crayfish, several hundred resident fishes, 150 juvenile shad.
2.3.1.2 On 07 December USACE Fisheries, with continued assistance from USFWS, CRITFC, NOAA, BPA, and PSMFC, removed from the Junction Pool 24 adult steelhead, one salmon, several peamouth, suckers and whitefish, 40 sturgeon and 15 juvenile shad.  
2.3.1.3 One dead adult steelhead was found in the upper section of A-branch.
2.3.1.4 All live salmonids were released upstream.  All sturgeon were released downstream, at the new navlock.
3 RESEARCH  

3.1 NOAA- PIT tag detectors.  Vibration sensor remains installed on Spill bay 6. 

3.2 ODFW/WDFW sea lions.  Moved the forebay sea lion trap on 19 November.
3.3 Smith-Root sea lion array.  Array remains installed in the UMT occurred on 02 December.
3.4 WDFW Fish Counting.  Video counting at Washington Shore continues.  Video counting at Bradford Island concluded on 04 December when the ladder went to orifice flow.
4 FISHWAYS 

4.1 Project biologists inspected 06, 08, 10 December.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)- currently dewatered

	
	
	
	
	
	

	CASCADES ISLAND (CI)- nothing to report

	
	
	
	
	
	

	WASHINGTON SHORE (WS)

	All week
	PCC/monoliths
	Head differential,  entrances closed
	F1 OOS.  No stab plates installed.
	Stab plates installed starting 12/11, 12/14
	

	12/6
	Weir 37
	Reading <1.0’
	Unknown
	No action taken
	


4.2.1 PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.3 Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder.  

4.3.1 Temperatures are taken 01 March through 30 November. 
Table 3.  Bonneville Fishway Temperatures
	Date
	WS Avg
	BI Avg

	12/1-2/28
	NA
	NA


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 08 December.
4.5.2 The PH1 ice and trash sluiceway (ITS) remains dewatered.
4.5.2.1 The ITS concrete plate, located at the downstream edge of the ITS and covers access to an old wooden bulkhead, has been removed.  The bulkhead is scheduled for replacement this winter.

4.5.3 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  
4.5.3.1 NUE and SUE remain closed and NDE and SDE remain full open.

4.5.4 11 of 12 floating orifice gates (FOG) remain installed at PH2.  One gate was removed for maintenance and replaced with a bulkhead.
4.5.4.1 Stab plate installation began on 11 December.  Three gates were completed on 11 December.  Installation will be completed on 14 December.
4.6 Juvenile Fishways.
4.6.1 The B2CC remains closed.
4.6.2 DSM1 wall and orifice removal continues.
4.6.3 DSM2 orifice 14C returned to auto.
4.7 Lamprey Fishways.  All LPSs have been dewatered.
4.7.1 The Cascades Is. entrance weir and slot filler remain installed.  
4.7.2 The PH2 NDE ramp remains in the lowered position.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  Crane rails replacement continues.  New crane in FY11.  
5.2 PH1 Ice and Trash Sluiceway Wall Removal.  Wall removal continues.  DSM1 outfall removal cancelled.
5.3 TIE crane.  Load testing occurred the week of 29 November.
6 HAZMAT, SPILLS AND CLEANUP.   Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010 to support chum spawning below the dam.  

7.3 A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.
7.4 A teletype sent on 05 November requests BON tailwater elevation hard constraint of no less than 11.3’ msl during all hours and a soft constraint of 11.3’ to 11.7’, with a target of 11.5’, from 0600 until 1700 daily.  This is effective from 0600 on 06 November until further notice.  This request is to provide necessary flows for chum spawning.  
JERRY CARROLL
Acting Operations Manager
Page 1 of 3
1
Page 3 of 3

[image: image1.wmf][image: image2.wmf][image: image3.wmf]