CENWP-OD-B






















02 March 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 09 of 2010, which covers the period from 21 through 27 February 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 110.5 to 127.6 kcfs.  Daily average project tailwater ranged from 11.4’ to 11.6’ msl.  Daily average powerhouse forebay elevation ranged from 76.1’ to 76.3’ msl.  Daily average river temperature ranged from 42 to 43ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 0.3 to 1.3 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse.
1.3.1 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

1.3.2 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.3 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.4 Unit 12 was out of service from 0124 on 22 February until 1654 on 23 February due to T11 outage and STS installation.

1.3.5 Unit 13 was out of service from 0048 on 22 February until 1657 on 23 February due to T11 outage and STS installation.

1.3.6 Unit 14 was out of service from 0111 on 22 February until 1706 on 23 February due to T11 outage and STS installation.

1.3.7 Unit 15 was out of service from 1226 until 1505 on 22 February for STS installation and from 0927 until 1210 on 23 February for STS repair.

1.3.8 Unit 16 was out of service from 0658 until 0917 on 23 February for STS installation.

1.3.9 Unit 17 was out of service from 1218 until 1430 on 23 February for STS installation.

1.3.10 Unit 18 was out of service from 0952 until 1345 on 24 February for STS installation.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 returned to service at 0958 on 27 February.  It had been out of service since 01 December for 2-SJ1 work and annual maintenance.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week: 

2.1.1 FV1-1 returned to service at 1530 on 27 February.
2.1.2 FV 3-7, 3-9, 4-3, and 4-4 returned to service at 1500 on 26 February.
2.1.3 FV 5-3 and FV 5-4 were closed from 0600 until 1130 on 23 February to facilitate the installation of the Cascades Island lamprey ramp camera.
2.2 STS/VBS inspections.  The following STS/VBS inspections and removal occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-15
	2/22
	
	STSs installed

	16-17
	2/23
	
	STSs installed

	18
	2/24
	
	STSs installed


2.3 Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.
3 RESEARCH  

3.1 FFU- sea lion.  Observations began on 08 January.  Weekly reports of sea lion activity will be available from Fisheries Field Unit starting in February. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801.
3.2 NOAA- PIT tag detectors.  Vibration sensor remains installed on Spill bay 6. 

3.3 NOAA lamprey.  Cascades Island lamprey ramp camera was installed on 23 February.

3.4 ODFW/WDFW sea lions.  Sea lion traps remain in position.  Trapping has not begun.
3.5 PSMFC.  Smolt monitoring is scheduled to being on 1 March.

3.6 Smith-Root sea lion array.  Array remains installed in the UMT. Testing is scheduled for the week of 1 March.
3.7 WDFW Fish Counting.  Video counting continues at WA shore and Bradford Island.  
3.8 WDFW, ODFW, CRITFC Sea lion hazing.  Hazing of Steller sea lions has been occurring on a limited basis since mid-January.  Hazing of California sea lions will begin on 01 March.

4 FISHWAYS 

4.1 Project biologists inspected 23, 25-26 February.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	2/23
	Bay 1
	On sill
	LPS camera install (see 3.3)
	Corrected when complete
	

	2/24
	PH2
	Unit priority
	Switchgear testing
	Corrected when complete
	

	BRADFORD ISLAND (BI)- nothing to report

	CASCADES ISLAND (CI)

	2/23
	CI entrance
	Differential <1.0’
	LPS camera install
	Corrected when complete
	

	2/23
	FV 5-3, 5-4, 5-9
	Closed or throttled down
	LPS camera install
	Corrected when complete
	

	2/23
	UMT weir
	Reading <1.0’
	LPS camera install
	Corrected when complete
	

	WASHINGTON SHORE (WS) – nothing to report


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 25 February.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  

4.5.2.1 NUE remains closed but will be opened by 1 March.  The other gates are adjusted as needed.  
4.5.3 Stab plates remain installed in 11 of 12 FOGs.  One gate remains out for maintenance, with a bulkhead installed.  Stab plates are scheduled to be removed the week of 01 March.
4.5.4 Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances. 
4.6 Juvenile Fishways.
4.6.1 The B2 Corner Collector remains closed. Concrete repairs are complete, and concrete is curing.
4.6.2 DSM2 was in service by 1100 on 18 February.  The SMF remains in bypass.
4.6.3 The PH1 ice and trash sluiceway (ITS) watered up at 1510 on 26 February.  The automated chaingates are open and in manual due to issues with the PLC.  No manual chaingrates are open at this time due to the inability to raise the bottom leaf of the ITS end gate. 
4.6.4 The hydrocannon is scheduled to be in service on 01 March.
4.7 Lamprey Fishways.  All LPSs have been dewatered.
4.7.1 The Cascades Is. entrance weir remains installed.  
4.7.2 The PH2 NDE ramp remains in the lowered position.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in FY11.  
5.2 PH1 Ice and Trash Sluiceway Wall Removal. Wall removal is complete.  Channel transducers were to be tested and calibrated the week of 21 February.  Outfall removal has been postponed.
5.3 TIE crane.  TIES are scheduled to be installed the week of 01 March.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 08 January requests BON forebay maintain 71.5’ to 77.0’ msl as a soft constraint, and 71.5’ to 77.5’ msl as a hard constraint from 0001 on 09 January until 1800 on 31 March.  This is a modification of the 01 September teletype.  This request is to reduce the risk of flooding machinery and twisting bollards at BON locks, while still supporting spillwall construction at TDA.
7.3 A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

7.4 A teletype sent on 30 December requests BON tailwater elevation be maintained at no less than 11.5’ msl during all hours.  This is effective from 1600 on 30 December until further notice.  This request is to provide necessary flows for chum egg incubation.

7.5 While conducting fishway inspections, Project biologists observed four kelts on 23 February at the north end of PH2 forebay and one kelt on 23 February in the vicinity of the B2CC bulkhead.
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 3
1
Page 3 of 3

