CENWP-OD-B






















31 May 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 22 of 2010, which covers the period from 23 through 29 May 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 171.9 to 239.5.8 kcfs.  Daily average project tailwater ranged from 15.6’ to 19.6’ msl.  Daily average powerhouse forebay elevation ranged from 74.3’ to 75.2’ msl.  Daily average river temperature ranged from 56 to 57ºF.  Secchi disk measurements ranged from 5.5’ to 6.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 99.3 to 99.6 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse. 
1.3.1 Unit 5 was out of service from 0758 until 0945 on 27 May for Unit 7 relay and electrical testing.  

1.3.2 Unit 6 was out of service from 0758 until 0945 on 27 May for Unit 7 relay and electrical testing.  

1.3.3 Unit 7 has remained out of service since 04 June 2007 for turbine rehab.  1% violations on 27 and 28 May for unit testing.  See FPP, Bon Appendix A, section 1.3.
1.3.4 Unit 8 was out of service from 0048 until 1601 on 26 May for Unit 7 phase verification.  Out of service from 0758 until 0945 on 27 May for Unit 7 relay and electrical testing.  
1.3.5 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.6 Unit 11 has remained out of service since 12 June 2008 due to rotor damage. 

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  No AWS valves were closed this reporting week. 
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Scheduled for week of 01 June


2.3 Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.
3 RESEARCH  

3.1 Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays complete. Tagged fish releases upstream have begun for dam passage and survival evaluations. Sort by Code operations at the SMF continued this week to evaluate acoustic tagging effects on juvenile salmonids.
3.2 CRITFC- sea lion. Deployed hydrophones on 01 March in BON tailraces to track sea lion activity.

3.3 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

3.4 FFU- sea lion.  Observations continue.  Weekly reports of sea lion activities are now available. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801. 

3.5 NOAA- lamprey.  Bradford Is. and WA Shore ladder AWS lamprey passage structures remain in service.  Cascades Island lamprey ramp camera remains installed.  Installed one inch spacers on the bottoms of the WA shore pickets leads at the count station on 25 May.  
3.6 PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  159 steelhead, 12 salmon, and 16 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  Two juvenile lamprey collected for University of Idaho researchers this week.  
3.7 WDFW- Fish Counting.  Visual counting continues.
3.8  WDFW, ODFW, CRITFC- Sea lion hazing/trapping.  Hazing from boats continues.  Sea lion traps were removed from the corner collector area and moved to the old nav lock channel for storage but animals continued to use them. State crews trapped seven California sea lions at this location.  Two were eligible for removal and the others were branded and released. One trap remains in the forebay.
3.9  USDA Wildlife Services- Sea lion hazing.  Hazing from shore continues.

3.10 USDA Wildlife Services- Avian hazing.  Hazing from shore continues.

3.11 University of Idaho – lamprey.   Two juvenile lamprey collected from PSMFC SMP this reporting week. 

3.12 University of Idaho - Adult salmon sampling continues for monitoring passage effects at the modified Cascades Island entrance.
4 FISHWAYS 

4.1 Project biologists inspected 23-29 May.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	5/25,29
	BI Weir
	Reading <1.0’
	Unknown
	Operators adjusted
	

	CASCADES ISLAND (CI) – Nothing to report

	WASHINGTON SHORE (WS)

	5/26
	PH2 entrances
	Differential <1.0’
	Swapping FOGs
	
	

	5/23, 28,29
	PH2 entrances
	Gate submerged <13’
	Gates in manual
	Operators adjusted
	


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.2.3 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	5/23
	53.7
	54.6

	5/24
	53.5
	54.4

	5/25
	53.9
	54.9

	5/26
	54.3
	55.1

	5/27
	54.5
	55.5

	5/28
	54.3
	55.1

	5/29
	53.9
	54.7


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 29 May.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.
4.5.3 Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  The repairs on one FOG have been completed.  Another FOG was removed for maintenance, with a bulkhead installed in its place.

4.5.4 Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances. 
4.5.5 Sampling at the AFF continues.  The downstream exit bulkhead remained in the lowered position after sampling this week to keep the ladder in criteria and shad off the weir 37 bleed off valve.  The automatic blow down function for the weir 37 bleed off valve was programmed on 19 May to operate every six hours.  
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service.  
4.6.3 Hydrocannon remains in service.
4.6.4 TIES are installed.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.  
4.7.2 The PH2 NDE ramp remains in the lowered position.  Pumps remain off.
4.7.3 Bradford Island and WA Shore LPS’s remain in service.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in FY11.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to occur in late summer.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 09 April requests spill for juvenile fish passage begin at 0001 hours on Saturday, 10 April and continue until further notice. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2010 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30 kcfs, then operate to minimum discharge and spill to pass inflow.  

GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 3
1
Page 2 of 3

