CENWP-OD-B






















06 May 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 23 of 2010, which covers the period from 30 May through 05 June 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 212.5 to 331.0 kcfs.  Daily average project tailwater ranged from 17.9’ to 25.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.9’ to 75.6’ msl.  Daily average river temperature ranged from 56 to 57ºF.  Secchi disk measurements ranged from 3.0’ to 6.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 95.9 to 105.6 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse. 
1.3.1 Unit 7 has remained out of service since 04 June 2007 for turbine rehab. Returned to service at 1434 on 03 June.  
1.3.2 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.3 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.4 Unit 18 was out of service from 1300 until 1515 on 04 June for manual cleaning of VBS’s with gantry crane.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 was on standby from 0008 until 0307 on 02 June and 0015 until 0216 on 05 June to float debris.

1.4.2 F2 was on standby from 0007 until 0312 on 02 June and 0017 until 0213 on 05 June to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week. 
2.1.1  All valves were reported clean by 1624 on 03 June.  FV 3-9 and FV 6-9 were briefly closed.  
2.2 STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12
	6/1
	849
	OK 

	13
	6/1
	512
	OK

	14
	6/1
	633
	OK

	15
	6/1
	832
	OK

	16
	6/1
	402
	OK

	17
	6/1
	812
	OK

	18
	6/1
	861
	OK


2.3 Dewatering and Fish Salvage.  The following dewatering/fish salvage activities occurred this week:
2.3.1 Unit 18 gatewells were dipped prior to cleaning VBS’s with the gantry crane.  Several hundred yearling chinook and juvenile sockeye were released into DSM2 in good condition upon release.  Six mortalities were recovered from the dipping basket and were returned to the river.  
3 RESEARCH  

3.1 Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays complete. Tagged fish releases upstream have begun for dam passage and survival evaluations. Sort by Code operations at the SMF continued this week to evaluate acoustic tagging effects on juvenile salmonids.
3.2 CRITFC- sea lion. Deployed hydrophones on 01 March in BON tailraces to track sea lion activity.  Utilizing video technology for monitoring.  
3.3 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

3.4 FFU- sea lion.  The final weekly report of sea lion activities was sent out on 28 May. If you would like information, please contact Robert Stansell-541-374-8801. 

3.5 NOAA- lamprey.  PIT tagging adult lamprey in the AFF began this week.  
3.6 PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  96 steelhead, nine salmon, and six unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  One juvenile lamprey collected for University of Idaho researchers this week.  
3.7 WDFW- Fish Counting.  Visual counting continues.
3.8 WDFW, ODFW, CRITFC- Sea lion hazing/trapping.  Hazing from boats concluded on 31 May.  Sea lion traps remain in the old navigation lock channel for storage. There are currently no reports of sea lions present at Bonneville project.
3.9  USDA Wildlife Services- Sea lion hazing.  Hazing from shore concluded on 31 May. 
3.10 USDA Wildlife Services- Avian hazing.  Hazing from shore continues.

3.11 University of Idaho – lamprey.   One juvenile lamprey collected from PSMFC SMP this reporting week.  Radio and PIT tagging adult lamprey in the AFF.
3.12 University of Idaho - Adult salmon sampling continues for monitoring passage effects at the modified Cascades Island entrance.
4 FISHWAYS 

4.1 Project biologists inspected 30 May – 05 June.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	6/2
	BI Weir
	Reading <1.0’
	Unknown
	Operators adjusted
	

	5/31
	PH1 SCC
	Entrance diff <1.0
	Unknown
	Operators adjusted
	

	CASCADES ISLAND (CI) – Nothing to report

	WASHINGTON SHORE (WS)

	5/31, 6/5
	PH2 entrances
	Gate submerged <13’
	Gates in manual
	Operators adjusted
	


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.2.3 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	5/30
	54.3
	55.2

	5/31
	54.9
	55.8

	6/1
	55.4
	56.2

	6/2
	55.5
	56.5

	6/3
	55.3
	56.3

	6/4
	55.3
	56.3

	6/5
	55.7
	56.6


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 04 June.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.
4.5.3 Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  The repairs on one FOG have been completed.  Another FOG was removed for maintenance, with a bulkhead installed in its place. With no sea lions currently present, the exclusion bars will be removed as soon as possible.
4.5.4 Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances. With no sea lions currently present, the SLEDs will be removed as soon as possible.
4.5.5 Sampling at the AFF continues.  The downstream exit bulkhead remained in the lowered position after sampling this week to keep the ladder in criteria and shad off the weir 37 bleed off valve.  The automatic blow down function for the weir 37 bleed off valve was programmed on 19 May to operate every six hours.  
4.5.6 WA shore and Cascades Is. ladder were put into operation for shad passage on 02 June.  
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service.  
4.6.3 Hydrocannon remains in service.
4.6.4 TIES are installed.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.  Cascade Is. LPS was put in service on 31 May.  Scheduled to operate Sunday night through Friday.  
4.7.2 The PH2 NDE ramp remains in the lowered position and was put in service on 31 May.  Will typically operate Sunday night through Friday.
4.7.3 Bradford Island and WA Shore LPS’s remain in service.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in FY11.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to occur in late summer.
6 HAZMAT, SPILLS AND CLEANUP.  A contractor working at Powerhouse 2 had a line rupture on one of their cranes on 2 June. The spill was noticed immediately and the contractor began dispensing absorbents but the control room was not immediately notified.  Once the Corps Environmental lead was on site, the oil had entered a drain that fed directly to the river.  It was heavily raining at the time of the spill. More absorbents were placed at the input and outlet of this drain system. Overall, the spill consisted of approximately 2 quarts of hydraulic oil with 1 quart entering the river.  All required reporting was done to the appropriate agencies.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 09 April requests spill for juvenile fish passage begin at 0001 hours on Saturday, 10 April and continue until further notice. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2010 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30 kcfs, then operate to minimum discharge and spill to pass inflow.  

GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 1
1
Page 3 of 3

