CENWP-OD-B






















13 June 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 24 of 2010, which covers the period from 06 through 12 June 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 336.2 to 397.7 kcfs.  Daily average project tailwater ranged from 26.1’ to 28.6’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 74.7’ msl.  Daily average river temperature ranged from 58 to 59ºF.  Secchi disk measurements ranged from 2.0’ to 3.5’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 122.0 to 195.1 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse. 
1.3.1 Unit 8 went out of service at 0655 on 08 June for servo repairs and four year overhaul.
1.3.2 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.3 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 was on standby to float debris from 0005-0214 on 06 June, 0002-0204 on 07 June, 0003-0201 on 08 June, 0002-0208 on 09 June, and 0101-0330 on 10 June.
1.4.2 F2 was on standby to float debris from 0005-0212 on 06 June, 0003-0206 on 07 June, 0003-0202 on 08 June, 0004-0210 on 09 June, and 0101-0331 on 10 June.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week. 
2.1.1 FV 3-7 was closed for cleaning from 1357 until 1527 on 07 June.

2.1.2 FV 3-9 was reported clean by 1557 on 07 June and was closed from 1457 until 1506 on 10 June for cleaning.

2.1.3 FV5-3 was cleaned on 12 June.

2.1.4 FV 5-9 was reported clean by 1017 on 07 June and 1531 on 10 June.

2.1.5 FV 6-9 was reported clean by 1531 on 10 June.

2.2 STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for week of 29 June
VBSs were cleaned as frequent as possible from 07-12 June.


2.3 Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.
3 RESEARCH  

3.1 Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays complete. Tagged fish releases upstream have begun for dam passage and survival evaluations. Sort by Code operations at the SMF continued this week to evaluate acoustic tagging effects on juvenile salmonids.
3.2 CRITFC- sea lion. Deployed hydrophones on 01 March in BON tailraces to track sea lion activity.  
3.3 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.
3.4 NOAA- lamprey.  PIT tagging adult lamprey in the AFF continues.  
3.5 PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  43 steelhead, 12 salmon, and 12 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  Three juvenile lamprey collected for University of Idaho researchers this week.  
3.6 WDFW- Fish Counting.  Visual counting continues.
3.7 USDA Wildlife Services- Avian hazing.  Hazing from shore continues.
3.8 University of Idaho – lamprey.   Three juvenile lamprey collected from PSMFC SMP this reporting week.  Radio and PIT tagging adult lamprey in the AFF.
3.9 University of Idaho - Adult salmon sampling continues for monitoring passage effects at the modified Cascades Island entrance.
4 FISHWAYS 

4.1 Project biologists inspected 06 - 12 June.  NOAA inspected on 11 June.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	6/11-12
	A & B-branch weir
	Reading >1.3’
	Unknown
	No action
	

	6/6-8
	BI fishway
	Not in shad passage mode
	Valve not programmed
	Electricians re-programmed valve
	

	6/10-12
	FV3-7 & 3-9 trashrack
	Drawdown > 0.5’
	Debris
	Riggers cleaned
	

	CASCADES ISLAND (CI)

	6/10
	UMT weir
	Reading <1.2’
	Unknown
	Operators adjusted
	

	6/11
	FG 6-14
	Diffuser closed
	Programming error
	Operators corrected
	

	6/11-12
	FV5-9 trashrack
	Drawdown > 0.5’
	Debris
	Riggers cleaned
	

	WASHINGTON SHORE (WS)

	6/11-12
	Weir 67
	Reading <1.0’
	Unknown
	Operators adjusted
	


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 Design of a mechanical velocity meter at the PH2 south monolith is in progress.  

4.2.3 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	6/6
	56.3
	57.2

	6/7
	56.3
	57.2

	6/8
	56.4
	57.4

	6/9
	56.3
	57.2

	6/10
	56.3
	57.2

	6/11
	56.7
	57.6

	6/12
	57.6
	58.5


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 11 June.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.
4.5.3 Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

4.5.4 Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances. The SLEDs will be removed as soon as possible.
4.5.5 Sampling at the AFF continues.  The downstream exit bulkhead remained in the lowered position after sampling this week to keep the ladder in criteria and shad off the weir 37 bleed off valve.  The automatic blow down function for the weir 37 bleed off valve was programmed on 19 May to operate every six hours.  
4.5.6 WA shore and Cascades Is. ladder remain in shad passage mode.
4.5.7 Bradford Island fishway was placed in shad passage mode on 08 June. 

4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service.  
4.6.3 Hydrocannon remains in service.
4.6.4 TIES remain installed.
4.6.5 Increased flow and debris during the week, and wind limitations with operating the TIE crane resulted in Maintenance crews not installing the secondary VBS behind the primary VBS during cleaning operations on 11 June while using the gantry crane.  Crews had been cleaning constantly throughout the week, and VBS differential criteria resulted in some units being operated at reduced load until the VBSs could be cleaned.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.  Cascade Is. LPS was shut down on 07 June due to a failed hoist.  It is expected to return to service on 14 June. Scheduled to operate Sunday night through Friday.  
4.7.2 The PH2 NDE ramp remains in the lowered position. It was shut down on 04 June due to high tailwater. Normally scheduled to operate Sunday night through Friday.  
4.7.3 Bradford Island and WA Shore LPS’s remain in service.
4.7.4 The WA shore LPS exit was modified on 7-8 June due to lamprey mortalities.  See 100607 MFR.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in FY11.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to begin on 06 July.
6 HAZMAT, SPILLS AND CLEANUP.  In support of the Ambursen Section construction, BON Project opened one of the old Nav Lock drains for the lower miter gate to lower the water level inside the lock on 07 June. All equipment was inspected prior to operation.  After the valve had been opened for 20 minutes (1315), a sheen started bubbling up from the area of the discharge pipe.  The sheen was 150 yds x 50 yds and heavily dispersed. Estimate release was 3/4 gal. Potential of the hydraulic unit is approximately 35 gallons.  The hydraulic equipment was immediately secured and control room notified.  The tail race of the old Nav Lock has two sections of hard boom permanently installed at the lower end.  Most of the sheen is being blown up against the miter gate and held there.  A sorbent boom was placed across the waterway under the road bridge.   An operator entered the area and inspected the hydraulic unit and found no visible leaks coming from the machinery. NRC #943124, OERS #10-1282, WDOE #10-1673.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 09 April requests spill for juvenile fish passage begin at 0001 hours on Saturday, 10 April and continue until further notice. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2010 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30 kcfs, then operate to minimum discharge and spill to pass inflow.  
7.3 A teletype sent on 11 June requests that Bonneville forebay be operated for the treaty fishery as follows:  0600 Wednesday, 16 June until 1800 Friday, 18 June and 0600 Tuesday, 22 June until 1800 Thursday, 24 June – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.  
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 3
1
Page 2 of 3

