CENWP-OD-B






















09 August 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 32 of 2010, which covers the period from 01 through 07 August 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 120.5 to 162.1 kcfs.  Daily average project tailwater ranged from 10.6’ to 14.1’ msl.  Daily average powerhouse forebay elevation ranged from 75.2’ to 76.1’ msl.  Daily average river temperature ranged from 70 to 71ºF.  Secchi disk measurements ranged from 5.5’ to 6.5’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 74.7 to 84.7 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse. 
1.3.1 Unit 0 went out of service at 0841 on 02 August for five year overhaul.
1.3.2 Unit 5 was out of service from 0900 on 01 August until 1319 on 04 August for annual maintenance. 
1.3.3 Unit 8 went out of service at 0900 on 01 August for rehab follow on work.  

1.3.4 Unit 9 has remained out of service since 04 August 2008 for turbine rehab.
1.3.5 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.6 Unit 13 went out of service at 0733 on 14 June for four-year overhaul.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F2 was out of service from 0759 until 1149 on 03 August for ROV PH2 fishway inspections.

1.4.2 F1 was out of service from 0806 until 1141 on 03 August for ROV PH2 fishway inspections.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV1-1 was closed from 0804 until 1155 on 04 August for ROV PH1 fishway inspections.

2.1.2 FV3-7 was closed from 0804 until 1155 on 04 August for ROV PH1 fishway inspections.

2.1.3 FV3-9 was closed from 0804 until 1155 on 04 August for ROV PH1 fishway inspections.
2.2 STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	NA


2.3 Dewatering and Fish Salvage.  The following dewatering/fish salvage activity occurred this week:
2.3.1 Biologists recovered one lamprey from Unit 0 draft tube on 02 August.  It was released upstream in good condition.
3 RESEARCH  

3.1 Battelle – survival study.  Monitoring acoustic tagged fish passage continues.  Sort by Code operations at the SMF continued this week to evaluate acoustic tagging effects on juvenile salmonids.  No fish collected.  
3.2 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  Modified sampling protocols were implemented on 05 August due to water temperatures >70.0’.  See Appendix G in the 2010 FPP for details.
3.3 NOAA- lamprey.  PIT tagging adult lamprey in the AFF continues.  
3.4 PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  one salmon.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  Modified sampling protocols were implemented on 06 August due to water temperatures >70.0’.  See Appendix J in the 2010 FPP for details.
3.5 WDFW- Fish Counting.  Visual counting continues.  Night counts continue.
3.6 USDA Wildlife Services- Avian hazing.  Hazing from shore concluded 30 July.

3.7 University of Idaho – lamprey.   Radio and PIT tagging adult lamprey in the AFF.
4 FISHWAYS 

4.1 Project biologists inspected 01-07 August.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) Nothing to report

	CASCADES ISLAND (CI) Nothing to report

	WASHINGTON SHORE (WS)

	8/5
	PH2 entrance gates
	Submerged <13’
	In manual
	Operators adjusted
	

	
	
	
	
	
	


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average
	AFF average
	SMF average

	8/1
	68.9
	68.8
	68.8
	69.0

	8/2
	69.2
	69.3
	69.1
	69.4

	8/3
	69.2
	69.3
	69.1
	69.5

	8/4
	69.5
	69.6
	69.4
	69.7

	8/5
	70.3
	70.4
	70.2
	70.5

	8/6
	70.5
	70.7
	70.4
	70.8

	8/7
	70.3
	70.5
	70.2
	70.6


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 07 August.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.
4.5.3 Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

4.5.4 Sampling at the AFF continues. Modified sampling protocols were implemented on 05 August due to water temperatures >70.0’.  See Appendix G in the 2010 FPP for details. http://www.nwd-wc.usace.army.mil/tmt/documents/fpp/2010/changes/APPG_TRAP_Revised_20100519.pdf
4.5.5 Operators continue to maintain 0.5’ of head at the PH2 fishway entrances for lamprey passage during night hours.  Table Bon-5 of the FPP is being utilized as a guideline. 
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service.  PH1 ITS Chain gate 6C continues to stick at elevation 72.8’ msl due to slack cable troubles. As forebay elevations fluctuate, the gate does not adjust as programmed.
4.6.3 Chain gate 6C was closed and 7A opened at 0740 on 04 August as outlined in the teletype sent on 29 July (See 7.3).  Chain gate 7A is set to 72’ msl.
4.6.4 Hydrocannon remains in service.
4.6.5 TIES remain installed.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains in service. Scheduled to operate Sunday night through Friday.
4.7.2 The PH2 NDE ramp remains in the lowered position and in service. 
4.7.3 Bradford Island and WA Shore LPS’s remain in service.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in FY11.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to occur on 11 August.
6 HAZMAT, SPILLS AND CLEANUP.  Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 16 July requests BON project begin the summer spill at 0430 on 21 July until 2400 on 31 August.  Spill 75kcfs during the day and gas cap at night.  Day time hours are defined in table BON-5 of the 2010 FPP.  Spill in accordance with pattern in table BON-16 of the 2010 FPP.  If flows are insufficient, the project is requested to reduce to minimum generation at night and spill the remainder.  The minimum generation requirement is 30 kcfs, and the minimum spill level is 50 kcfs
7.3 A teletype sent on 29 July requests BON project change PH1 unit priority as follows: 1, 3,7,6,2,4,5,8,10,9, effective immediately until further notice.  This moves Unit 7 to third in priority.  This operation is necessary to complete a 100 day operation per PH1 rehab contract.  The project is requested to close automatic chain gate 6C and open manual gate 7A to minimize impacts to fish passage.
7.4 A teletype sent on 6 August requests Bonneville pool be held at or above 77 feet from 1400 to 2000 hrs on 14 August as a soft constraint to allow sail boats participating in a regatta to be pulled from the water at The Dalles boat ramp.
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 3
1
Page 3 of 3

