CENWP-OD-B





















04 October 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 40 of 2010, which covers the period from 26 September through 02 October 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 75.9 to 112.5 kcfs.  Daily average project tailwater ranged from 7.7’ to 10.2’ msl.  Daily average powerhouse forebay elevation ranged from 74.3’ to 76.1’ msl.  Daily average river temperature ranged from 66 to 68ºF.  Secchi disk measurements averaged 7.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill averaged 1.4 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse. 
1.3.1 Unit 0 has remained out of service since 02 August for five year overhaul.
1.3.2 Unit 1 has remained out of service since 17 September due to sticking wicket gates.  
1.3.3 Unit 7 had a 1% violation on 29 September for air gap monitor testing.
1.3.4 Unit 9 has remained out of service since 04 August 2008 for turbine rehab. Unit 9 had a 1% violation on 27 September due to testing. Unit 9 was in operation from 1649 on 28 September until 1647 on 01 October for 72 hours heat load test.
1.3.5 Unit 10 returned to service at 1325 on 25 September.  It had been out of service since 21 September due to Bank 9/10 outage for Unit 9 reconnect.
1.3.6 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.7 Unit 12 has remained out of service since 13 September for four year overhaul.

1.3.8 Unit 14 was out of service from 2030 on 26 September until 1556 on 27 September due to unit brake control circuit.  
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

2.1.1 FV 1-1 was closed for cleaning from 1550 until 1603 on 01 October.
2.1.2 FV 3-7 was closed for cleaning from 0954 until 1045 on 30 September.

2.1.3 FV 3-9 was closed for cleaning from 0715 until 0745 on 28 September, from 1350 until 1400 on 28 September, and from 1522 until 1525 on 29 September.
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for the week of 18 October.


2.3 Dewatering and Fish Salvage. No dewatering and fish salvage activities occurred this week.
3 RESEARCH  

3.1 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  
3.2 PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  The SMF was placed in bypass from 1835 on 29 September until 1645 on 30 September.  See 4.6.6. for more detail.  Fallbacks recorded crossing the separator bars for this reporting week: 14 salmon and 2 unknown salmonids.  Truck releases from McNary Dam, Lower Granite, Little Goose, and Lower Monumental dams continue.
3.3 WDFW- Fish Counting.  Visual counting continues.  Nighttime counts concluded on 30 September.
3.4  WDFW- Tule counting.  Tule counting concluded on 01 October.
4 FISHWAYS 

4.1 Project biologists inspected 26 September through 02 October.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	All week
	BI fish exit
	Needs cleaning
	Aquatic vegetation
	Riggers cleaned on 27-30 September and 01 October twice per day.
	

	9/27,30
10/2
	B-branch entrance
	Differential <1.0’
	System in manual
	Operators adjusted.
	

	9/28-29
	BI picket leads
	Drawdown > 0.3’
	Aquatic vegetation
	Riggers cleaned.
	

	9/30
	A-branch weir
	Reading >1.0’
	Unknown
	No action taken.
	

	          CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS) - Nothing to report.


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average
	AFF average
	SMF average

	9/26
	64.8
	65.1
	64.8
	65.4

	9/27
	65.1
	65.4
	65.1
	65.6

	9/28
	65.6
	66.0
	65.6
	66.2

	9/29
	66.0
	66.4
	66.0
	66.5

	9/30
	66.3
	66.6
	66.2
	66.8

	10/1
	66.1
	66.4
	66.1
	66.6

	10/2
	66.0
	66.4
	66.1
	66.6


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 02 October.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.
4.5.3 Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

4.5.4 Sampling at the AFF continues.  
4.5.5 The Bradford Island fish exit was closed for cleaning from 0715 until 0745 on 28 September, from 1522 until 1525 on 29 September, and from 0751 until 0810 on 30 September.
4.5.6 The Washington Shore fish exit was closed for cleaning from 0704 until 0708 on 29 September.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 B2CC remains closed for the season.
4.6.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 6C was closed and 7A opened at 0740 on 04 August as outlined in the teletype sent on 29 July (See 7.2).  Chain gate 7A is set to 72’ msl.
4.6.4 Hydrocannon remains in service.
4.6.5 Three TIES remain installed.  Two TIEs were removed the week of 19 September, and one was removed on 29 September.  The remaining TIES are scheduled for removal the week of 03 October.
4.6.6 The SMF was placed in bypass from 1835 on 29 September until 1645 on 30 September due to inaccurate DSM2 channel elevation sensors.  This was done due to the potential for fluctuating flows at the SMF and dewatering screens while the water level sensors were being repaired.  DSM2 was placed in manual operation from 1340 until 1705 to allow maintenance crews to replace the faulty PLC board for the DSM2 channel elevation sensors and to attempt repairs on the auto trip function for the ERG.  Currently, the ERG does not have an auto trip function.  Further repairs are scheduled to occur the week of 03 October.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.
4.7.2 The PH2 NDE ramp remains in the lowered position and is not currently operating.
4.7.3 Bradford Island and WA Shore LPS’s remain in service.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in FY11.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls within 50’ of the Cascades Island fishway is scheduled to resume when fish counts drop below 1,000.
5.3 PH1 juvenile outfall removal.  Removal work above water line is scheduled to occur mid-October.  In-water work is scheduled to occur between 1-10 November.
5.4 BGS removal. Scheduled to occur in early December.
5.5 NDE lamprey modifications. Contractor will begin mobilizing on 15 November.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 29 July requests BON project change PH1 unit priority as follows: 1, 3,7,6,2,4,5,8,10,9, effective immediately until further notice.  This moves Unit 7 to third in priority.  This operation is necessary to complete a 100 day operation per PH1 rehab contract.  The project is requested to close automatic chain gate 6C and open manual gate 7A to minimize impacts to fish passage.
7.3 A teletype sent on 24 September requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Monday, 27 September until 1800 Wednesday, 29 September.   This is to limit pool fluctuation and reduce wear and tear on equipment.
7.4 A teletype sent on 28 September requests Bonneville forebay be maintained between 73.0’-74.5’ msl, hard constraint, and 73.0’-74.0’ msl, soft constraint, from 0600 until 1700 on 02 October.  This operation was requested to support the Gorge Games in Hood River.

7.5 Bonneville Fisheries sent out the following Memorandum’s for the Record:

7.5.1 100927: Two chinook mortalities found on the Valve 15 trashrack.  One fish had been sampled by CRITFC on 24 September and appeared to recover from anesthesia at that time.  CRITFC noted some lamprey and parasite marks during sampling.
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 1
1
Page 3 of 3

