CENWP-OD-B





















17 October 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 42 of 2010, which covers the period from 10 through 16 October 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 100.9 to 126.4 kcfs.  Daily average project tailwater ranged from 9.8’ to 11.5’ msl.  Daily average powerhouse forebay elevation ranged from 74.4’ to 75.1’ msl.  Daily average river temperature ranged from 63 to 65ºF.  Secchi disk measurements ranged from 6.1 to 7.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.3 to 1.5 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse. 
1.3.1 Unit 0 has remained out of service since 02 August for five year overhaul.
1.3.2 Unit 1 has remained out of service since 17 September due to sticking wicket gates.  
1.3.3 Unit 2 went out of service at 0920 on 05 October for five year overhaul.

1.3.4 Unit 4 was out of service from 1330 on 10 October until 1810 on 15 October due to BPA 230kV transmission MW restriction.

1.3.5 Unit 8 was out of service from 1330 on 10 October until 1810 on 15 October due to BPA 230kV transmission MW restriction.
1.3.6 Unit 9 returned to service at 1510 on 13 October.  It had been out of service since 04 August 2008 for turbine rehab. Unit 9 was out of service from 1206 until 1437 on 14 October due to generator heater repair.
1.3.7 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.8 Unit 12 has remained out of service since 13 September for four year overhaul.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

2.1.1 FV 1-1 was closed for cleaning from 0758 until 0808 on 12 October.
2.1.2 FV 3-9 was closed for cleaning from 1537 until 1600 on 14 October, and from 1015 until 1035 on 15 October.
2.1.3 FV 5-9 was closed for cleaning from 1344 until 1400 on 14 October.

2.1.4 FV 6-9 was closed for cleaning from 1523 until 1535 on 14 October.

2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week:
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for the week of 18 October.


2.3 Dewatering and Fish Salvage. The following fish salvage activities occurred this week:
2.3.1 On 14 October, Fisheries recovered five bass, two sculpin, and seven crawdads from the Unit 0 tail logs.  All fish were released in good condition.
3 RESEARCH  

3.1 CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  
3.2 PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week: 19 salmon, three unknown salmonids, and two steelhead.  Truck releases from Lower Granite, Little Goose, and Lower Monumental dams continue.
3.3 WDFW- Fish Counting.  Visual counting continues. 
4 FISHWAYS 

4.1 Project biologists inspected 10 through 16 October.
4.2  Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	10/14,15
	FV 3-9 trashrack
	Needs cleaning
	Aquatic vegetation
	Riggers cleaned 10/14, 15
	

	10/13
	A-branch weir
	Reading >1.0’
	Unknown
	No action taken.
	

	          CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS)

	10/12-13, 16
	Weir 38
	Reading <1.0’
	Unknown
	No action taken.
	


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	10/10
	63.7
	64.0

	10/11
	63.4
	63.8

	10/12
	62.6
	62.9

	10/13
	61.8
	62.2

	10/14
	62.0
	62.4

	10/15
	61.6
	62.0

	10/16
	61.4
	61.7


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 16 October.
4.5.2 The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.
4.5.3 Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

4.5.4 Sampling at the AFF continues.  
4.5.5 The Bradford Island fish exit was closed for cleaning from 1537 until 1600 on 14 October, and from 1015 until 1035 on 15 October.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 B2CC remains closed for the season.
4.6.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 6C was closed and 7A opened on 04 August as outlined in the teletype sent on 29 July (See 7.2).  Chain gate 7A is set to 72’ msl.
4.6.4 Hydrocannon returned to service on 13 October due to increased bird predation and the need to protect truck-released fish from upriver dams.
4.6.5 Three TIES were removed on 14 October.  All six TIES have now been removed.  
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.
4.7.2 The PH2 NDE ramp remains in the lowered position and is not currently operating.
4.7.3 Bradford Island and WA Shore LPS’s remain in service.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in FY11.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls within 50’ of the Cascades Island fishway is scheduled to resume when fish counts drop below 1,000.
5.3 PH1 juvenile outfall removal.  Removal work above water line began on 11 October.  In-water work is scheduled to occur between 1-10 November.
5.4 BGS removal. Scheduled to begin mid-December.
5.5 NDE lamprey modifications. Contractor will begin mobilizing on 15 November.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 29 July requests BON project change PH1 unit priority as follows: 1, 3,7,6,2,4,5,8,10,9, effective immediately until further notice.  This moves Unit 7 to third in priority.  This operation is necessary to complete a 100 day operation per PH1 rehab contract.  The project is requested to close automatic chain gate 6C and open manual gate 7A to minimize impacts to fish passage.
7.3 A teletype sent on 07 October requests BON project limit outflow to 90 kcfs or less from 0700 until 1600 on 11 October.  As a hard constraint, BON outflow should not exceed 100 kcfs during this time.  This operation is requested to support removal of the juvenile bypass release pipe downstream of PH1.
7.4  A teletype sent on 08 October requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Monday, 11 October until 1800 Wednesday, 13 October.   This is to limit pool fluctuation and reduce wear and tear on equipment.
7.5 A teletype sent on 14 October requests BON project change PH1 unit priority as follows: 1, 10, 9, 3,7,2,6,4,5,8, effective immediately until further notice. This moves unit 9 to third in priority, and replaces the teletype sent on 29 July (see 7.2). This operation is necessary to complete a 100 day operation per PH1 rehab contract.

7.6 A teletype sent on 15 October requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Tuesday, 19 October until 1800 Thursday, 21 October.   This is to limit pool fluctuation and reduce wear and tear on equipment.
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 3
1
Page 2 of 3

