CENWP-OD-B





















20 December 2010
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 51 of 2010, which covers the period from 12 December through 18 December 2010.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 131.4 to 204.0 kcfs.  Daily average project tailwater ranged from 14.3’ to 18.5’ msl.  Daily average powerhouse forebay elevation ranged from 72.6’ to 75.1’ msl.  Daily average river temperature was 43ºF.  Secchi disk measurements ranged from 4.0 to 5.5’.
1.2 Spill Bay 18, which provides attraction flow for B-branch, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 29.9 kcfs.  

1.3 Unit Operation.  Powerhouse One is the priority powerhouse. 
1.3.1 Unit 1 has remained out of service since 17 September due to sticking wicket gates.  
1.3.2 Unit 2 went out of service at1218 on 12 December due to a Kaplan oil leak, contained in the powerhouse.
1.3.3 Unit 9 went out of service at 0430 on 17 December due to a Kaplan oil leak, contained in the powerhouse.
1.3.4 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.5 Unit 12 returned to service at 1651 on 14 December.  It had been out of service since 13 September for four year overhaul.  Unit 12 was out of service from 2024 on 14 December until 1557 on 15 December due to a broken 12A STS plug.  Unit 12 was out of service from 0430 until 1635 on 16 December, and from 0430 until 1530 on 17 December for BGS removal.
1.3.6 Unit 13 was out of service from 0400 until 1708 on 13 December, from 0400 until 1501 on 14 December, from 0430 until 1516 on 15 December, from 0430 until 1656 on 16 December, and from 0430 until 1530 on 17 December for BGS removal.

1.3.7 Unit 14 was out of service from 0400 until 1707 on 13 December, from 0400 until 1517 on 14 December, from 0430 until 1531 on 15 December, from 0430 until 1620 on 16 December, and from 0430 until 1530 on 17 December for BGS removal.

1.3.8 Unit 15 was out of service from 0400 until 1719 on 13 December, from 0400 until 1530 on 14 December, from 0430 until 1524 on 15 December, from 0430 until 1613 on 16 December, and from 0430 until 1530 on 17 December for BGS removal.

1.3.9 Unit 16 was out of service from 0400 until 1708 on 13 December, from 0400 until 1530 on 14 December, and from 0430 until 1530 on 17 December for BGS removal.

1.3.10 Unit 18 was out of service from 0430 until 1620 on 15 December, and from 0430 until 1719 on 16 December for BGS removal.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 and F2 remain out of service while the WS fishway is dewatered. 

1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

2.1.1 FV 1-1 was closed for cleaning from 0720 until 0724 on 17 December.  FV 1-1 was closed to float debris from 2140 on 12 December until 0430 on 13 December.
2.1.2 FV 3-7 was closed for cleaning from 0800 until 0858 on 15 December.  FV 3-7 was closed to float debris from 2140 on 12 December until 0430 on 13 December.
2.1.3  FV 3-9 was closed for cleaning from 0723 until 0736 on 13 December, from 0712 until 0724 on 15 December, and from 0658 until 0702 on 17 December. 
2.1.4 FV 4-3 and 4-4 were closed to flush debris through the spillway from 1215 until 1500 on 15 December.
2.1.5 FV 5-3, 5-4, and 5-9 remain closed while the Cascades Island fishway is dewatered.
2.1.6 FV 6-9 remains closed while the WS fishway is dewatered.
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12
	12/15
	NA
	STS removed.

	13
	12/17
	NA
	STS removed.

	14
	12/16
	NA
	STS removed.

	15
	12/16
	NA
	STS removed.

	16
	12/16
	NA
	STS removed.

	17
	12/20
	NA
	STS removed.

	18
	12/17
	NA
	STS removed.


2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.
3 RESEARCH  
3.1 WDFW- Fish Counting.  Video counting continues.
4 FISHWAYS 

4.1 Project biologists inspected 13 through 17 December.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) 

	12/15
	PH1 entrances
	Differential <1.0’
	Unknown
	Ops adjusted
	

	12/15
	FG 3-5
	Incorrect position
	Unknown
	Ops adjusted
	

	12/15
	Chaingate 10B
	Incorrect position
	Unknown
	Ops adjusted
	

	12/16
	B-branch entrance
	Reading >2.0’
	PLC malfunction
	Ops adjusted
	11-51508

	CASCADES ISLAND (CI) – Nothing to report

	WASHINGTON SHORE (WS) – Nothing to report


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.
4.2.3 The PH1 PCC mechanical velocity meter remains out for maintenance crews to use as a template while constructing a new one.

4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 17 December.
4.5.2 The Washington Shore and Cascades Island fish ladders remain dewatered. 
4.5.3 Stab plates or bulkheads remain installed in the floating orifice gates (FOGs) while the WS fishway remains dewatered. One FOG remains out for maintenance.
4.5.4 The Bradford Island fish exit was closed for cleaning from 0723 until 0736 on 13 December, and from 0800 until 0858 on 15 December.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.  DSM2 is scheduled to be dewatered on 21 December.
4.6.2 B2CC remains closed for the season.  It is scheduled to briefly open on 22 December to test the new boat exclusion boom in the PH2 forebay.
4.6.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 1A, 1B, and 10B remain open (see section BON 2.5.1.1.m. in the 2010 FPP).
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.
4.7.2 The PH2 NDE ramp remains in the lowered position and is not currently operating.
4.7.3 Bradford Island and WA Shore LPS’s remain out of service for the season.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in Spring, 2011.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls continues.

5.3 BGS removal. Construction began on 07 December.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 14 October requests BON project change PH1 unit priority as follows: 1,10,9,3,7,2,6,4,5,8, effective immediately until further notice. This moves Unit 9 to third in priority, and replaces the teletype sent on 29 July that moved Unit 7 to third in priority. This operation is necessary to complete a 100 day operation per PH1 rehab contract.

7.3 A teletype sent on 10 December outlines a forebay exceedence above the normal 76.5’ msl.  From noon on 11 December until noon on 18 December, the maximum forebay elevation is 77’ msl.  This operation is needed to meet tailwater elevation for chum (see 7.3) with the forecasted high inflows and rising Willamette flows.

7.4 Teletypes sent on 13, 14, 15, and 17 December modifies the 19 November chum tailwater teletype:

7.4.1 Effective immediately until further notice, hard constraint of no less than 12.1’ msl during all hours, and a hard constraint of 12.1’ to 12.5’ with a target of 12.3’, from 0630 until 1700 daily. 

7.4.2 If needed, BON is authorized to pass water in excess of what is necessary to meet the 12.1’ to 12.5’ hard constraint by increasing tailwater elevation to 18.5’ msl between 1700 and 0600 hours.  Normal ramp rates apply.  It is preferred to concentrate the highest tailwater around midnight without exceeding 16.5’ msl.

7.4.3 If the actions above are not sufficient, tailwater elevations may increase incrementally by 0.5’, as necessary, up to 18.5’ msl between 0600 and 1700 hours, daily.  The bottom of the range may become the new tailwater minimum.
7.4.4 From 0630 until 1700 daily from 14 through 1730 on 20 December, BON is authorized to increase tailwater to 18.3’ to 18.7’ msl.  Spill will be required.  As soon as inflows allow, the Project will return to the operations outlined in 7.6.2.
7.5 Teletypes sent on 15 December revise the teletype sent on 07 December and requests limited generation at PH2 for BGS removal.  Limit PH2 flow to 2 units from 0500 to 1700 daily on 16, 17, 20, and 21 December.  Unit priority for these flows should be 17, 18.  Diving may be terminated at 1500 on 16 and 17 December if high flow conditions continue.  Spill is authorized to maintain chum tailwater elevation requirements.     
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 3
1
Page 2 of 3

