CENWP-OD-B





















18 January 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 02 of 2011, which covers the period from 09 through 15 January 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 150.8 to 188.6 kcfs.  Daily average project tailwater ranged from 13.4’ to 16.9’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 75.0’ msl.  Daily average river temperature ranged from 37 to 40ºF.  Secchi disk measurements ranged from 6.0 to 7.0’.
1.2 Spill Bay 18, which provides attraction flow for B-branch, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 0.8 kcfs.  

1.3 Unit Operation.  Powerhouse One is the priority powerhouse. 
1.3.1 Unit 1 has remained out of service since 17 September due to sticking wicket gates.  
1.3.2 Unit 2 was out of service from 2219 on 04 January until 1251 on 06 January due to upper guide bearing overheat.
1.3.3 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 and F2 remain out of service while the WS fishway is dewatered. 

1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV 3-7 was closed for cleaning from 1522 until 1605 on 14 January.

2.1.2 FV 3-9 was closed for cleaning from 0705 until 0715 on 10 January.

2.1.3 FV 5-3, 5-4, and 5-9 remain closed while the Cascades Island fishway is dewatered.
2.1.4 FV 6-9 remains closed while the WS fishway is dewatered.
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	STSs scheduled to be reinstalled the week of 22 February.


2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.
3 RESEARCH  
3.1 WDFW- Fish Counting.  Video counting continues.
4 FISHWAYS 

4.1 Project biologists inspected 10 through 14 January.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) 

	1/10, 14
	B-branch entrance
	Differential < 1.0’
	B-branch entrance sensor failure
	See 4.2.3
	11-69379

	1/14
	A-branch weir
	 > 1.1’
	Unknown
	Ops adjusted
	

	CASCADES ISLAND (CI) – Dewatered

	WASHINGTON SHORE (WS) – Dewatered


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 The PH1 PCC mechanical velocity meter remains out for maintenance crews to use as a template while constructing a new one.
4.2.3 The B-branch entrance sensor is malfunctioning.  The fishway is currently operating in manual as electricians address the problem.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 14 January.

4.5.2 The Washington Shore and Cascades Island fish ladders remain dewatered. 
4.5.3 Stab plates or bulkheads remain installed in the floating orifice gates (FOGs) while the WS fishway remains dewatered. One FOG remains out for maintenance.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains dewatered for winter maintenance.
4.6.2 B2CC remains closed for the season.
4.6.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 1A, 1B, and 10B remain open.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.
4.7.2 The PH2 NDE ramp remains in the lowered position and is not currently operating.
4.7.3 Bradford Island and WA Shore LPS’s remain out of service for the season.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in June, 2011.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls continues.

6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 14 October requests BON project change PH1 unit priority as follows: 1,10,9,3,7,2,6,4,5,8, effective immediately until further notice. This moves Unit 9 to third in priority, and replaces the teletype sent on 29 July that moved Unit 7 to third in priority. This operation is necessary to complete a 100 day operation per PH1 rehab contract.
7.3 A teletype sent on 22 December outlines new tailwater operations for chum incubation.  Effective immediately, BON is requested to maintain a tailwater of 12.2’ or greater for all hours.
7.4 A teletype sent on 22 December notifies BON that slow roll start-up for units that have been idle for 12 hours or more is required from 01 December through 30 April (see FPP section BON 5.7). 
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 2
1
Page 2 of 2

