CENWP-OD-B





















07 February 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 05 of 2011, which covers the period from 30 January through 05 February 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 176.6 to 244.1 kcfs.  Daily average project tailwater ranged from 15.8’ to 19.5’ msl.  Daily average powerhouse forebay elevation ranged from 71.8’ to 72.7’ msl.  Daily average river temperature ranged from 39 to 40ºF.  Secchi disk measurements ranged from 2.0 to 5.0’.
1.2 Spill Bay 18, which provides attraction flow for B-branch, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 6.2 kcfs. 

1.3 Unit Operation.  Powerhouse One is the priority powerhouse. 
1.3.1 Unit 1 has remained out of service since 17 September due to sticking wicket gates.  Unit 1 was operated briefly for testing on 02 and 03 February.  The unit remains out of service. 
1.3.2 Unit 2 was out of service from 1052 until 1354 on 02 February to rake trash.

1.3.3 Unit 4 was out of service from 0820 until 1319 on 01 February to rake trash.

1.3.4 Unit 6 was out of service from 1356 until 1539 on 02 February to rake trash.

1.3.5 Unit 8 was out of service form 0820 until 1157 on 03 February to rake trash.

1.3.6 Unit 10 was out of service from 1541 until 1633 on 02 February to rake trash.

1.3.7 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.8 Unit 18 was out of service from 0803 until 1218 on 26 January for cooling water strainer inspection.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.4.1 F1 and F2 remain out of service while the WS fishway is dewatered. 

1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV 3-7 was closed for cleaning from 0815 until 0858 on 31 January and from 0725 until 0736 on 03 February.
2.1.2 FV 3-9 was closed for cleaning from 0725 until 0736 on 03 February.

2.1.3 FV 4-3 and 4-4 were closed from 0855 until 1255 on 03 February for and ROV inspection.

2.1.4 FV 5-3, 5-4, and 5-9 remain closed while the Cascades Island fishway is dewatered.
2.1.5 FV 6-9 remains closed while the WS fishway is dewatered.
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	STSs scheduled to be reinstalled the week of 22 February.


2.3 Dewatering and Fish Salvage.  No fish salvage activities occurred this week.
3 RESEARCH  
3.1 FFU - Sea lion.  Observations began on 07 January.
3.2 ODFW - Sea lion trapping. Moved sea lion traps adjacent to the B2CC and downstream of the old Navlock on 27 January.  Trapping has not begun for the season.
3.3 WDFW - Fish Counting.  Video counting continues.
4 FISHWAYS 

4.1 Project biologists inspected 31 January, 01, 02, and 04 February.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) 

	01/31, 02/01
	B-branch entrance
	Differential > 2.0’
	System in manual
	Ops adjusted
	

	01/31
	FV 1-1 trashrack
	Drawdown > 0.5’
	Debris
	Riggers cleaned
	

	CASCADES ISLAND (CI) – Dewatered

	WASHINGTON SHORE (WS) – Dewatered


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 The PH1 PCC mechanical velocity meter remains out for maintenance crews to use as a template while constructing a new one.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 04 February.
4.5.2 The Washington Shore and Cascades Island fish ladders remain dewatered. 
4.5.3 Stab plates or bulkheads remain installed in the floating orifice gates (FOGs) while the WS fishway remains dewatered. One FOG remains out for maintenance.
4.5.4 SLEDs are installed at PH1 and B-branch entrances.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains dewatered for winter maintenance.
4.6.2 B2CC remains closed for the season.
4.6.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Chaingates 1A, 1B, and 10B remain open. Chaingates 4A and 7A were opened on 22 January to assist in floating trash.

4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.
4.7.2 The PH2 NDE ramp remains in the lowered position and is not currently operating.
4.7.3 Bradford Island and WA Shore LPS’s remain out of service for the season.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in June, 2011.  
5.2 Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls continues.

6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.
7.2 A teletype sent on 14 October requests BON project change PH1 unit priority as follows: 1,10,9,3,7,2,6,4,5,8, effective immediately until further notice. This moves Unit 9 to third in priority, and replaces the teletype sent on 29 July that moved Unit 7 to third in priority. This operation is necessary to complete a 100 day operation per PH1 rehab contract.
7.3 A teletype sent on 22 December outlines new tailwater operations for chum incubation.  Effective immediately, BON is requested to maintain a tailwater of 12.2’ or greater for all hours.
7.4 A teletype sent on 22 December notifies BON that slow roll start-up for units that have been idle for 12 hours or more is required from 01 December through 30 April (see FPP section BON 5.7). 
7.5 A teletype sent on 03 February replaces the teletype sent on 14 October (see 7.2).  Effective immediately until further notice, BON unit priority is: 1,10,3,6,2,4,5,8,7,9,11,18,12,17,13,14,15,16.  Unit 9 testing is complete.

7.6 A teletype sent on 03 February outlines the operation of the B2CC on 09 February from 0700 to 1630.  If sufficient debris has passed prior to 1630, a call will be made to close the B2CC.  If necessary, the B2CC can be opened on 10 February from 0700 to 1630. If sufficient debris has passed prior to 1630, a call will be made to close the B2CC.  This operation is necessary to flush debris in the PH2 forebay.
7.7 Project Fisheries received notice from Fish Field Unit on 03 February of three sturgeon mortalities associated with Unit 1 testing.  A memorandum for the record will be sent out on 08 February.
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 1
1
Page 3 of 3

