CENWP-OD-B





















24 April 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 16 of 2011, which covers the period from 17 through 23 April 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 259.2 to 303.7 kcfs.  Daily average project tailwater ranged from 21.2’ to 23.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.4’ to 74.4’ msl.  Daily average river temperature ranged from 46 to 47ºF.  Secchi disk measurements ranged from 2.0’ to 3.5’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 99.5 to 99.8 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse.
1.3.1 Unit 5 was out of service from 0116 on 19 April until 1630 on 20 April to replace oil head O-ring.

1.3.2 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.
1.5 Gatewell drawdowns are measured on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  No AWS valves were closed this reporting week.
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.
Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for week of 05 May.


2.3 Dewatering and Fish Salvage.  The following fish salvage activity occurred this reporting week:

2.3.1 On 20 April project biologists recovered 14 juvenile steelhead, 2 chinook yearlings, and 1 coho juvenile from Unit 5 headgates. Fish were released into the ITS in good condition.
3 RESEARCH  
3.1 Battelle - survival study.  Hydrophone installation complete.  Tagging scheduled to start the week of 25 April.
3.2 CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF began on 19 April.
3.3 CRITFC - Sea lion hazing.  Hazing from boats continues.  Acoustic receivers for sea lion tags anchored in BRZ.  Video camera system for sea lion observation set up at PH2 south monolith.
3.4 FFU - Sea lion.  Observations continue.  Weekly pinniped reports can be found at

http://www.nwd-wc.usace.army.mil/tmt/documents/fish/2011/sea_lion_hazing2011.html
3.5 Kintama Research.  Acoustic tagging yearling Chinook at the SMF began this week.  500 fish were collected from PSMFC SMP sampling. 
3.6 NOAA- B2CC PIT.  PIT tag detector testing complete. 
3.7 NOAA - COE Walla Walla District transportation evaluation.  Sort by Code collections at the SMF continue.
3.8 NOAA - lamprey. DIDSON mount installed on the NDE LPS on 15 February.  
3.9 ODFW/WDFW - Sea lion trapping. Sea lion traps remain adjacent to the B2CC and downstream of the old Navlock.  Acoustic tagging and branding continues. 
3.10 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  18 steelhead and two unknown salmonids.  Please see http://www.fpc.org/adultsalmon/bonkeltcounts.htm for updated kelt counts.  Spring Creek fish arrived at BON at approx. 2250 on 12 April. The majority of fish passed the project by 15 April. The average mortality rate was 1.3%, just under the historical norm of 1.5% for the Spring Creek passage. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  
3.11 WDFW - Fish Counting.  Visual counting continues.
3.12 USDA - Sea lion and avian hazing. Hazing from the deck continues.
4 FISHWAYS 
4.1 Project biologists inspected 17 through 23 April. 
4.2 Fish Passage Plan Observations.
5 Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) 

	4/17, 21, 22
	Auto chain gate 6C
	Operating incorrectly
	Slack rope trouble
	Operations adjusted.
	

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS) – Nothing to report.


5.1.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

5.1.2 The PH1 PCC mechanical velocity meter has been repaired and a new mechanical velocity meter has been fabricated for PH2. Both are scheduled for installation.
5.1.3 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.
5.2 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	4/17
	45.6
	46.1

	4/18
	45.9
	46.3

	4/19
	46.0
	46.4

	4/20
	46.1
	46.6

	4/21
	46.2
	46.6

	4/22
	46.3
	46.7

	4/23
	46.5
	47.0


5.3 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
5.4 Adult Fishways. 
5.4.1 Calibration was checked on 23 April.
5.4.2 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

5.4.3 SLEDs remain installed at all fishway entrances.
5.4.4 The AFF was watered up on 13 April.
5.5 Juvenile Fishways.
5.5.1 DSM2 remains in service.
5.5.2 The PH1 ice and trash sluiceway (ITS) remains in service.  Manual chaingates 1A and 1B remain open. Automated chaingates 6C and 10B are open and functioning in auto.  Chaingate 3B remains in manual. Parts to repair 3B and return it to auto have been ordered and will be installed upon arrival.
5.5.3 The hydrocannon remains in service.
5.5.4 The B2CC remains in service.  One avian line remains broken.  
5.6 Lamprey Fishways.
5.6.1 The Cascades Is. entrance weir remains installed.  The CI LPS remains out of service.
5.6.2 The NDE ramp remains in the lowered position and is not currently operating.
5.6.3 Bradford Island and WA Shore LPS’s remain out of service.
6 CONSTRUCTION
6.1 PH1 Gantry 4.  New crane in August, 2011.
6.2 Spillway Gate Repair Pit. Clean-up of hazardous material and shoring of the walls is complete.  Load test scheduled to occur spring 2011.
6.3 B2CC Hoist. Construction scheduled to begin fall of 2011.
7 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
8 TELETYPES AND OTHER NOTEWORTHY ITEMS
8.1 A teletype sent on 22 December outlines new tailwater operations for chum incubation.  Effective immediately, BON is requested to maintain a tailwater of 12.2’ or greater for all hours.

8.2 A teletype sent on 22 December notifies BON that slow roll start-up for units that have been idle for 12 hours or more is required from 01 December through 30 April (see FPP section BON 5.7).  Note: Though specified in the FPP and the teletype as only occurring when units have been idle for 12 or more hours, Bonneville has been starting all idle units with slow roll protocol.  
8.3 A teletype sent on 08 April requests spill for juvenile fish passage begin at 0001 hours on Sunday, 10 April and continue through 20 June at 2400 hours. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2011 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30-40 kcfs, then operate to minimum discharge and spill to pass inflow.

8.4 A teletype sent on 08 April requests special operations for Spring Creek and Little White Salmon hatchery releases on 12 April.  Beginning 0600 on 13 April until 1700 on 17 April as a hard constraint and from 1700 on 17 April until 1700 on 21 April as a soft constraint, operate PH2 units at the lower 25-50% range of the 1% limit.
8.5 A teletype sent on 14 April updated the teletype referenced in 8.4 and added that if additional generation is needed, fully load PH1 units within the 1% range.  Then operate PH2 units with in the 25-50% range of the 1% limit as a hard constraint. If additional generation is needed then increase PH2 units one at a time in the 50-100% range of the 1% limit. The dates and times of these operations may be superseded by a request by the SMF.
8.6 A teletype sent on 20 April, effective immediately, lifted restrictions on BON tailwater for chum egg incubation as referenced in 8.1. 

8.7 A teletype sent on 21 April, effective immediately, cancelled soft constraints and other requirements for unit operation for the Spring Creek hatchery releases as stated in the teletype referenced in 8.4 and 8.5.
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 1
1
Page 2 of 3

