CENWP-OD-B





















29 May 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 21 of 2011, which covers the period from 22 through 28 May 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 470.7 to 498.1 kcfs.  Daily average project tailwater ranged from 31.0’ to 32.0’ msl.  Daily average powerhouse forebay elevation ranged from 71.9’ to 73.0’ msl.  Daily average river temperature stayed constant at 54ºF all week. Secchi disk measurements ranged from 1.0’ to 2.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 254.6 to 280.1 kcfs.
1.3 Unit Operation.  Powerhouse One remains the priority powerhouse.
1.3.1 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

1.3.2 Unit 12 was out of service from 0934 until 1210 on 26 May for STS removal.

1.3.3 Unit 13 was out of service from 0655 until 0946 on 25 May for STS removal.

1.3.4 Unit 17 was out of service from 1300 until 1455 on 24 May for STS removal.

1.3.5 Unit 18 was out of service from 1052 until 1255 on 24 May for STS removal.   Out of service from 0121 until 0926 on 26 May due to a turbine bearing lube oil leak. 
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.  This week required fish units to be placed on standby to float debris during daylight hours due to excessive drawdown of up to 10-12 ft.  
1.4.1 F1 was out of service from 1142 until 1720 on 25 May for a headgate oil leak inspection.

1.4.2 F2 was out of service from 1334 until 1523 on 25 May for trash raking.
1.5 Gatewell drawdowns are measured as needed and on Wednesdays.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:
2.1.1 FV 3-7 was closed for cleaning from 0908 until 0913 on 26 May.
2.1.2 FV 3-9 was closed for cleaning from 1303 until 1320 on 26 May.

2.1.3 FV 6-9 was closed for cleaning from 1336 until 1351 on 26 May. 

2.2 STS/VBS inspections.  The following STS/VBS inspection occurred on 23 May.
Table 1.  STS and VBS inspections.
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12
	05/23
	523
	OK

	13
	05/23
	523
	OK

	14
	05/23
	408
	OK

	15
	05/23
	433
	OK

	16
	05/23
	456
	OK

	17
	05/23
	524
	OK

	18
	05/23
	520
	OK


2.3 Dewatering and Fish Salvage.  No fish salvage activities occurred this reporting week.
3 RESEARCH  
3.1 Battelle - survival study.  Acoustic tagging and spring fish releases continue until 31 May.   
3.2 CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.
3.3 CRITFC - Sea lion hazing.  Hazing from boats has ended for the season.  Acoustic receivers for sea lion tags remain anchored in the BRZ.  Video camera system for sea lion observation at PH2 south monolith has been removed for the season.
3.4 FFU - Sea lion.  Daily observations concluded 27 May.  Weekly pinniped reports can be found at

http://www.nwd-wc.usace.army.mil/tmt/documents/fish/2011/sea_lion_hazing2011.html
3.5 Kintama Research.  Acoustic tagging yearling Chinook at the SMF continues.  150 yearling Chinook were collected from SMP sampling for research this week.
3.6 NOAA - COE Walla Walla District transportation evaluation.  Sort by Code collections at the SMF continue.
3.7 NOAA/PSMFC - lamprey.  LPS count network remains installed.  Traps deployed at PH2 monoliths in tailrace and AFF. 
3.8 ODFW/WDFW - Sea lion trapping. Sea lion trapping has ended for the season.  
3.9 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  16 steelhead, 15 salmon and 12 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  A total of 25 yearling Chinook and 25 coho were collected for NOAA research this week.  150 yearling Chinook were collected for Kintama.  
3.10 WDFW - Fish Counting.  Visual counting continues.
3.11 USDA - Sea lion and avian hazing. Hazing from the deck continues.

4 FISHWAYS 
4.1 Project biologists inspected 22 through 28 May. NOAA inspected on 27 May.
4.2 Fish Passage Plan Observations.
5 Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI) 

	5/23
	B-branch entrance
	Differential < 1.0.’
	High tailwater, entrance elev. sensor
	Operations adjusted.
	

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS)

	5/28
	PH2 B-diffusers
	Gates closed
	One fish unit ops for trash float on F2
	Operations returned to normal.
	

	5/25
	DSM2 orifice 13C-N
	Bad prox switch
	Unknown
	TR.
	11-173098


5.1.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

5.1.2 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
5.1.3 The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.
5.2 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	5/22
	53.3
	53.8

	5/23
	53.5
	53.9

	5/24
	53.6
	54.0

	5/25
	53.3
	53.7

	5/26
	52.6
	53.0

	5/27
	52.7
	53.1

	5/28
	52.9
	53.4


5.3 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
5.4 Adult Fishways. 
5.4.1 Calibration was checked on 27 May.
5.4.2 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

5.4.3 SLEDs remain installed at all fishway entrances.
5.4.4 The AFF remains watered up.
5.5 Juvenile Fishways.
5.5.1 DSM2 remains in service. 
5.5.2 Due to high flow and high debris load, elevated descaling was observed at the JMF starting 13 May, leading to a teletype requesting a change in operations on 19 May (see section 8.1). Powerhouse One became priority and STSs were removed on units 14, 15, and 16. Keeping VBS differentials below criteria and maximizing discharge at each unit was not achievable.  It was determined that the remaining STSs should be pulled on units 12, 13, 17, 18.  All STSs were removed by 26 May.
5.5.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.  
5.5.4 The hydrocannon remains in service.
5.5.5 The B2CC remains in service.  Five avian lines are broken due to high tailwater and three remain.  
5.6 Lamprey Fishways.
5.6.1 The Cascades Is. entrance weir remains installed.  The CI LPS remains out of service.
5.6.2 The NDE ramp remains in the lowered position and is not currently operating.
5.6.3 WA Shore LPS was watered up and operational on 25 May. Bradford Island LPS remains out of service.  It is scheduled to return to service the week of 29 May.  
6 CONSTRUCTION
6.1 PH1 Gantry 4.  New crane in August, 2011.
6.2 Spillway Gate Repair Pit. Clean-up of hazardous material and shoring of the walls is complete.  Load test scheduled to occur spring 2011.
6.3 B2CC Hoist. Construction scheduled to begin fall of 2011.
7 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
8 TELETYPES AND OTHER NOTEWORTHY ITEMS
8.1 A teletype sent on 19 May requests that BON operate Powerhouse One as the priority powerhouse. Continue this operation until further notice. The goal of this operation is to minimize debris loading that is contributing to increased descaling and mortality of juvenile fish at Powerhouse Two (PH2). Additionally, operate units 14, 15, and 16 without Submersible Traveling Screens. Vertical Barrier Screens (VBSs) will remain installed for these units until debris loading causes a drawdown of 1.5 ft. Once VBSs satisfy this criterion, remove VBSs in units 14, 15, and 16. When selecting operating range within the 1% range of the PH2 screened units (12, 13, 17, and 18) make efforts to the extent practicable to achieve the following two objectives: 1) Do not exceed the 1.5 ft head differential prior to the next cleaning and 2) Maximize discharge at each unit. Objective 1 takes priority over objective 2.
8.2 A teletype sent on 20 May requests the following operation at BON for the purposes of system flood control. Make the best effort to maintain outflows from BON near 465 kcfs, beginning at 0800 hrs, Friday, 20 May. Proceed to make the best effort to maintain flows near 470 kcfs on Saturday, 21 May, and 475 kcfs on Sunday, 22 May. On Monday, 23 May, ramp up outflow and maintain flows near 490 kcfs until further notice.
8.3 A teletype sent on 25 May, effective as early as system conditions allow, with a goal by 26 May and until further notice, requests that BON make best efforts to maintain outflows near 500 kcfs, with a range of 495 kcfs to 505 kcfs. The goal is to not exceed a max instantaneous flow of 505 kcfs. These flow requirements are necessary to maintain adequate system storage space, with operational flexibility provided primarily from Grand Coulee. These operations use best available modeling planning tools so as to minimize risks of major flooding during the peak of the Columbia freshet, forecast for early June.

8.4 A teletype sent on 26 May, effective as early as system conditions allow, with a goal by 27 May and until further notice, requests that BON make best efforts to maintain outflows near 510 kcfs, with a range of 505 kcfs to 515 kcfs. The goal is to not exceed a max instantaneous flow of 515 kcfs.
8.5 A teletype sent on 27 May, effective as early as system conditions allow, with a goal by 27 May and until further notice, requests that BON make best efforts to maintain outflows near 510 kcfs, with a range of 505 kcfs to 515 kcfs. The goal is to not exceed a max instantaneous flow of 515 kcfs. Then, beginning 28 May or earlier, and until further notice make best efforts to maintain outflows from BON near 520 kcfs, with a range of 515 to 525 kcfs. Goal is to not exceed a max instantaneous flow of 525 kcfs.
GLEN A. SMITH, P.E.
Operations Project Manager
Page 1 of 4
1
Page 4 of 4

