CENWP-OD-B





















31 July 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 30 of 2011, which covers the period from 24 through 30 July 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 225.5 to 266.8 kcfs.  Daily average project tailwater ranged from 18.5’ to 20.7’ msl.  Daily average powerhouse forebay elevation ranged from 73.8’ to 74.3’ msl.  Daily average river temperature ranged from 65 to 67ºF. Secchi disk measurements ranged from 4.0’ to 6.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 89.1 to 139.4 kcfs.
1.3 Unit Operation.  Powerhouse One remains the priority powerhouse.
1.3.1 Unit 3 was out of service from 0800 on 25 July to 1830 on 29 July for 230kV MW restriction.
1.3.2 Unit 4 went out of service at 0800 on 25 July for 230kV MW restriction.
1.3.3 Unit 5 went out of service at 0744 on 25 July for 230kV MW restriction.
1.3.4 Unit 6 went out of service at 0744 on 25 July for 230kV MW restriction.
1.3.5 Unit 7 went out of service at 0042 on 25 July for annual maintenance and Bank 7/8 bi-annual work.
1.3.6 Unit 8 went out of service at 0042 on 25 July for annual maintenance and Bank 7/8 bi-annual work.
1.3.7 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.8 Unit 14 was out of service from 0800 on 25 July to 1830 on 29 July for 230kV MW restriction.
1.3.9 Unit 15 went out of service at 0717 on 15 June for four year overhaul.
1.3.10 Unit 16 was out of service from 0800 on 25 July to 1830 on 29 July for 230kV MW restriction.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.    
1.5 Gatewell drawdowns are measured on Tuesdays and more frequently as needed.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  No AWS closures occurred this reporting week.
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week. 
2.3 Table 1.  STS and VBS inspections.
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for week of 14 Aug.


2.4 Dewatering and Fish Salvage.  No fish salvage activities occurred this reporting week.
3 RESEARCH  
3.1 Battelle - survival study.  Monitoring University of Idaho acoustic tagged adult lamprey.   
3.2 CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues. New sampling tank was installed 25-28 July. CRITFC resumed sampling in the AFF on 1 August.
3.3 CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.  
3.4 NOAA/PSMFC - lamprey.  LPS count network improvements moving forward.  Traps deployed at PH2 monoliths in tailrace and AFF. 
3.5 NOAA – Pathology Study. A total of 25 subyearling chinook were collected for NOAA pathology studies this week.
3.6 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  10 steelhead, 14 salmon, and 11 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  
3.7 University of Idaho.  Tagging lamprey in the AFF continues.

3.8 USDA - Avian hazing. Hazing concluded on 28 July.

3.9 WDFW - Fish Counting.  Visual counting continues.
3.10 WDFW – AFF. Modifications to the auxiliary sample flume and old sample tank continue. Sampling for alternative gear study control group scheduled to begin the week of 22 August. 
4 FISHWAYS 
4.1 Project biologists inspected 24 through 30 July.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	7/29
	A-branch
	Water level > 1.1’
	Unknown
	N/A
	

	7/29
	WG64
	Out of sub. criteria
	Broken counter
	TR
	11-219248

	7/29
	B-branch entrance
	Diff < 1.0’
	System in local
	Ops adjusted
	

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS)

	All week
	PH2 entrance gates
	Submergence <13’
	System in local
	Ops adjusted
	

	7/28
	DSM2 Screen cleaner #3
	Screen cleaner #3 OOS
	Tracking issues
	TR and adjusted air burst system to compensate
	11-219239


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
4.2.3 The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average
	AFF

average
	SMF

Average*

	7/24
	63.9
	64.3
	64.1
	65.2

	7/25
	64.2
	64.6
	64.3
	65.0

	7/26
	64.3
	64.7
	64.4
	65.1

	7/27
	64.1
	64.5
	64.3
	64.9

	7/28
	64.3
	64.8
	64.5
	65.1

	7/29
	64.9
	65.3
	65.0
	65.6

	7/30
	65.4
	65.9
	65.6
	66.2


*The temperature probe in the SMF may be malfunctioning. It is being investigated.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 29 July.
4.5.2 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance. 
4.5.3 SLEDs were removed from all entrance gates as of 05 July. 
4.5.4 The AFF remains watered up.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service. Mechanical screen cleaner #2 developed a faulty prox switch on 09 July. It was repaired and is now back in service.  Screen cleaner #3 went out of service on 28 July to replace worn guide bearings. Due to return to service the week of 1 August.
4.6.2 STSs for units 12 were installed on 11 July and on 12 July units 13 and 18 were installed. The remaining STSs for units 14, 16, and 17 were installed on 19 July. Unit 15 STSs will be installed when four year overhaul is complete (11 August).
4.6.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.
4.6.4 The hydrocannon was returned to service on 06 July.  
4.6.5 The B2CC remains in service.  Five avian lines are broken due to high tailwater and three remain.  
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.  The CI LPS is in operation on weekdays.
4.7.2  The NDE ramp remains in the lowered position and is not currently operating.
4.7.3 WA Shore and Bradford Island LPSs remain watered up.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in August, 2011.
5.2 B2CC Hoist. Construction scheduled to begin fall of 2011.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 15 June requests summer spill for juvenile fish passage with two treatments of 85 kcfs during the day and 121 kcfs at night or 95 kcfs for 24 hours.  Effective 16 June at 0430 hours and continuing until 31 August at 2400 hours, spill in accordance with the 2011 Fish Passage Plan and the 2011 Summer Fish Operations Plan, Appendix E of the Fish Passage Plan.  
7.2 A teletype sent on 07 July requests that BON forebay be maintained between elevation 75.5’ and 76.5’ as a hard constraint and 76.0’ and 76.5’ as a soft constraint from 1400 to 2000 hrs on Saturday, 06 August for a sail boat race. This request allows sail boats to be pulled from the water at the Dalles boat ramp after racing.

7.3 A teletype sent on 20 July states that, effective immediately, resume operation of Powerhouse 2 as the priority powerhouse as defined in the Fish Passage Plan.

7.4 A teletype sent on 22 July requests that Bonneville pool be operated as follows:  Operate within a 1.5 foot band, soft constraint, from 0600 hours Monday, 25 July until 1800 hours Saturday, 30 July.  The goal of this operation is to limit pool fluctuation during treaty fishing.
JERRY CARROLL
Operations Project Manager
Page 1 of 3
1
Page 2 of 3

