CENWP-OD-B





















07 August 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 31 of 2011, which covers the period from 31 July through 06 August 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 181.5.5 to 242.1 kcfs.  Daily average project tailwater ranged from 17.0’ to 19.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 76.0’ msl.  Daily average river temperature ranged from 67 to 69ºF. Secchi disk measurements ranged from 5.0’ to 6.7’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 90.0 to 92.0 kcfs.
1.3 Unit Operation.  Powerhouse Two remains the priority powerhouse.
1.3.1 Unit 4 went out of service at 0800 on 25 July for 230kV MW restriction. It returned to service at 1007 on 03 August.
1.3.2 Unit 5 went out of service at 0744 on 25 July for 230kV MW restriction. It returned to service at 1446 on 03 August.
1.3.3 Unit 6 went out of service at 0744 on 25 July for 230kV MW restriction. It returned to service at 1446 on 03 August.
1.3.4 Unit 7 went out of service at 0042 on 25 July for annual maintenance and Bank 7/8 bi-annual work.
1.3.5 Unit 8 went out of service at 0042 on 25 July for annual maintenance and Bank 7/8 bi-annual work.
1.3.6 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.7 Unit 13 was out of service from 0029 on 03 August until 1117 on 04 August for annual maintenance.
1.3.8 Unit 15 went out of service at 0717 on 15 June for four year overhaul. STSs for this unit were installed on 02 August.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 F1 was out of service from 0016 until 1721 on 03 August for slip ring maintenance and the ROV inspection. 
1.4.2 F2 was out of service from 0016 until 1724 on 03 August for slip ring maintenance and the ROV inspection.
1.5 Gatewell drawdowns are measured on Tuesdays and more frequently as needed.
2 ACTIVITIES

2.1 Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.
2.1.1 FV 1-1 was closed from 0830 until 1044 on 02 August for the ROV inspection.
2.1.2 FV 3-7 was closed from 0839 until 1044 on 02 August for the ROV inspection.

2.1.3 FV 1-1 and FV 3-7 were closed from 1255 until 1641 on 02 August for the ROV inspection.

2.1.4 FV 5-3 and FV 5-4 were closed from 1015 until 1130 on 04 August for the ROV inspection.
2.1.5 FV 4-3 and FV 4-4 were closed from 1245 until 1530 on 04 August for the ROV inspection.
2.2 STS/VBS inspections.  No STS/VBS inspections occurred this reporting week. 
2.3 Table 1.  STS and VBS inspections.
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for week of 14 Aug.


2.4 Dewatering and Fish Salvage.  No fish salvage activities occurred this reporting week.
3 RESEARCH  
3.1 Battelle - survival study.  Monitoring University of Idaho acoustic tagged adult lamprey.   
3.2 CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues. New sampling tank was installed 25-28 July. CRITFC resumed sampling in the AFF on 1 August.
3.3 CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.  
3.4 NOAA/PSMFC - lamprey.  LPS count network improvements moving forward.  Traps deployed at PH2 monoliths in tailrace and AFF. 
3.5 NOAA – Pathology Study. A total of 26 subyearling chinook were collected for NOAA pathology studies this week.
3.6 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  14 steelhead, 14 salmon, and 15 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  Truck releases of summer out-migrants originating from McNary began on 03 August.
3.7 University of Idaho.  Tagging lamprey in the AFF continues.

3.8 USDA - Avian hazing. Hazing concluded on 28 July.

3.9 WDFW - Fish Counting.  Visual counting continues.
3.10 WDFW – AFF. Modifications to the auxiliary sample flume and old sample tank continue. Sampling for alternative gear study control group scheduled to begin the week of 22 August. 
4 FISHWAYS 
4.1 Project biologists inspected 31 July through 06 August.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	8/2
	A-branch, PH1 N/S entrances, CC velocity
	All out of criteria
	ROV inspection
	N/A
	

	7/31-8/1
	WG64
	Out of sub. criteria
	Broken counter
	TR
	11-219248

	8/1, 3
	B-branch entrance
	Diff < 1.0’
	System in local
	Ops adjusted
	

	8/4
	B-branch SG, entrance
	All out of criteria
	ROV inspection
	N/A
	

	CASCADES ISLAND (CI)

	8/4
	UMT SG, entrance
	All out of criteria
	ROV inspection
	N/A
	

	WASHINGTON SHORE (WS)

	8/3
	SUE, SDE, NUE, NDE, CC velocity
	All out of criteria
	ROV inspection
	N/A
	

	8/6
	PH2 entrance gates NDE, SDE
	Submergence <13’
	Unknown, slack cable alarm
	TR
	11-220484
11-220488

	7/31-8/2
	DSM2 Screen cleaner #3
	Screen cleaner #3 OOS
	Tracking issues
	TR and adjusted air burst system to compensate
	11-219239

	8/6
	DSM2 Orifice 12B-N
	Closed
	Faulty prox open switch
	TR
	11-220489


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
4.2.3 The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average
	AFF

average
	SMF

Average*

	7/31
	65.7
	66.2
	65.9
	66.5

	8/1
	66.0
	66.4
	66.1
	66.7

	8/2
	66.2
	66.6
	66.4
	67.0

	8/3
	66.6
	67.0
	66.7
	67.3

	8/4
	67.0
	67.4
	67.1
	67.7

	8/5
	67.1
	67.5
	67.2
	67.8

	8/6
	67.1
	67.5
	67.2
	67.8


*The temperature probe in the SMF may be malfunctioning. It is being investigated.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 05 August.
4.5.2 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance. 
4.5.3 SLEDs were removed from all entrance gates as of 05 July. 
4.5.4 The AFF remains watered up.
4.5.5 A ROV inspection was conducted 02-04 August for Powerhouse 1 Collection Channel, Powerhouse 2 Collection Channel, B-branch entrance area, and Cascades Island entrance area. Diffuser shafts and diffuser grating were the main focus of the inspection. Three pieces of diffuser grating were found to be dislodged in the junction pool area and lower weirs in the north monolith of Powerhouse 2.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service. Screen cleaner #3 went out of service on 28 July to replace worn guide bearings. It was returned to service on 02 August.
4.6.2 STSs for units 12 were installed on 11 July and on 12 July units 13 and 18 were installed. The remaining STSs for units 14, 16, and 17 were installed on 19 July. Unit 15 STSs were installed on 02 August.
4.6.3 The PH1 ice and trash sluiceway (ITS) remains in service.  Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.
4.6.4 The hydrocannon was returned to service on 06 July.  
4.6.5 The B2CC remains in service.  Five avian lines are broken due to high tailwater and three remain.  
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.  The CI LPS is in operation 7 days a week.
4.7.2  The NDE ramp remains in the lowered position and was watered up on 27 July.
4.7.3 WA Shore and Bradford Island LPSs remain watered up.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  New crane in August, 2011.
5.2 B2CC Hoist. Construction scheduled to begin fall of 2011.
6 HAZMAT, SPILLS AND CLEANUP
6.1 On Wednesday 03 August, the intake gantry crane on the +90 deck of Powerhouse 1 developed an oil leak. A few drops of oil are suspected to have reached the ITS. The leak was quickly contained and repaired by 04 August.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 15 June requests summer spill for juvenile fish passage with two treatments of 85 kcfs during the day and 121 kcfs at night or 95 kcfs for 24 hours.  Effective 16 June at 0430 hours and continuing until 31 August at 2400 hours, spill in accordance with the 2011 Fish Passage Plan and the 2011 Summer Fish Operations Plan, Appendix E of the Fish Passage Plan.  
7.2 A teletype sent on 07 July requests that BON forebay be maintained between elevation 75.5’ and 76.5’ as a hard constraint and 76.0’ and 76.5’ as a soft constraint from 1400 to 2000 hrs on Saturday, 06 August for a sail boat race. This request allows sail boats to be pulled from the water at the Dalles boat ramp after racing.
JERRY CARROLL
Operations Project Manager
Page 1 of 4
1
Page 3 of 4

