CENWP-OD-B





















18 September 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 37 of 2011, which covers the period from 11 through 17 September 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 110.6 to 136.0 kcfs.  Daily average project tailwater ranged from 10.3’ to 12.3’ msl.  Daily average powerhouse forebay elevation ranged from 73.7’ to 75.1’ msl.  Daily average river temperature ranged from 68 to 70ºF. Secchi disk measurements ranged from 6.0’ to 7.0’.
1.2 Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.3 to 2.0 kcfs. On 16 September, spill bay 18 was set on sill at 1340 for emergency B-branch dewatering. Spill bay 1 was raised to 1’ open during daylight hours per teletype in section 7.4.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse.
1.3.1 Unit 9 went out of service at 0728 on 07 September for bearing replacement.
1.3.2 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.3 Unit 15 went out of service at 0719 on 05 September due to exciter failure.

1.3.4 Unit 16 went out of service at 0452 on 04 September due to exciter failure. 
1.3.5 Unit 17 went out of service at 1010 on 09 August due to generator vibration.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris. 
1.5 Gatewell drawdowns are measured on Tuesdays and more frequently as needed.
2 ACTIVITIES
2.1 Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.
2.1.1 FV 1-1 was closed for cleaning from 0714 until 0730 on 12 September.
2.1.2 FV 4-3 was closed for emergency B-branch dewatering at 1334 on 16 September.
2.1.3 FV 4-4 was closed for emergency B-branch dewatering at 1334 on 16 September.
2.1.4 FV 3-9 was closed for emergency B-branch dewatering at 1334 on 16 September.
2.2 STS/VBS inspections.  No STS/VBS inspection occurred this reporting week. 
2.2.1 Table 1.  STS and VBS inspections.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for week of 26 September


2.3 Dewatering and Fish Salvage. The following activity occurred this reporting week.
2.3.1 On 13 September Project Fisheries retrieved 1 sturgeon from the Unit 17 scroll case. The fish was deceased upon retrieval and returned to the tailrace.
2.3.2 On 17 September Project Fisheries with the assistance of District and Fish Field Unit personnel salvaged 19 salmonids and 3 white sturgeon from the B-branch ladder to allow dewatering to support the emergency repair.  All fish were released to the forebay in good condition
3 RESEARCH  
3.1 Battelle - survival study.  Monitoring University of Idaho acoustic tagged adult lamprey.   
3.2 CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues. 
3.3 CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.  
3.4 NOAA/PSMFC - lamprey.  LPS count network improvements moving forward. Cascades Island LPS trap and haul concluded on 15 September.
3.5 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Fallbacks recorded crossing the separator bars: 12 salmon, and 5 unknown salmonids. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  
3.6 University of Idaho.  Tagging lamprey in the AFF concluded in early September.
3.7 University of Washington – JMF. No fish were collected this week.

3.8 WDFW - Fish Counting.  Visual counting continues.
3.9 WDFW – Tule Counting. Tule counting began 17 August.
3.10 WDFW – AFF. Sampling for alternative gear study control group began 24 August. 
3.11 Yakama Fisheries – AFF. Coho energy study concluded 16 September. 
4 FISHWAYS 
4.1 Project biologists inspected 11 through 17 September.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	9/14
	B-branch entrance
	Diff > 2.0’
	System in local
	Ops adjusted
	

	9/12-17
	FG 3-27
	PLC indicates open but is closed
	Electrical issue
	TR
	

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS)

	All week
	SDE, NDE
	Will not lower past 3.5’
	Unknown, possible debris in gate slot
	TR
	11-220488

	9/12, 16
	Weir 37 bleed off
	Weir 37 staff gauge out of criteria
	No electrical operation
	TR
	11-247377

	9/11-14
	FV 6-9
	Valve not functioning in auto, Weir 67 staff gauge out of criteria
	Unknown
	TR
	11-234386


4.2.1 PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
4.2.3 The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work  replacing the PLC to allow for fully automated operation of the PH2 adult fishway will be complete by the end of the fiscal year.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average
	AFF

average
	SMF

Average

	9/11
	68.9
	69.2
	69.0
	69.7

	9/12
	68.8
	69.0
	68.8
	69.5

	9/13
	68.4
	68.6
	68.5
	69.2

	9/14
	67.9
	68.1
	68.1
	68.7

	9/15
	67.2
	67.4
	67.3
	68.0

	9/16
	66.7
	66.6
	66.8
	67.5

	9/17
	66.4
	62.7*
	66.5
	67.3


* Bradford Island B-branch was dewatered on 17 September.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 16 September.
4.5.2 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance. 
4.5.3 SLEDs were removed from all entrance gates as of 05 July. 
4.5.4 The AFF remains watered up.
4.5.5 B-branch was set at orifice flow on the afternoon of 16 September and dewatered on 17 September. It remains out of service. See section 7.4 and MFR 110919 BON B-branch emergency dewater for more information.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service. 
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.
4.6.3 The hydrocannon was returned to service on 06 July.  
4.6.4 The B2CC was closed 01 September.  Five avian lines are broken due to high tailwater and three remain. 
4.6.5 Spill ended on 01 September.
4.6.6 Truck releases of summer out-migrants originating from McNary began on 03 August. Truck releases from Lower Granite, Little Goose and Lower Monumental dams were inaugurated on 17 August.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.  
4.7.2 The CI LPS was taken out of service for the season on 15 September.
4.7.3  The NDE ramp is out of service for the season.
4.7.4 WA Shore and Bradford Island LPSs remain watered up.
5 CONSTRUCTION
5.1 PH1 Gantry 4.  The new crane arrived on project 12 September. The old gantry was removed and the new gantry was put in place on 15 September. Old crane pieces are scheduled to be removed on 19 September with testing of the new gantry to follow.
5.2 B2CC Hoist. Construction scheduled to begin fall of 2011.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 26 August requests that on Saturday, 17 September, 2011 from 0800 to 1600 hours, BON forebay be maintained in a 1.5 foot band of 72.0 feet - 73.5 feet as a hard constraint. It is also requested as a soft constraint to maintain the BON pool in a 1 foot band of 72.0 feet -73.0 feet for the same date and times. This operation will assist a clean-up event at the mouth of the White Salmon river to remove abandoned boats and trash that could be washed downstream when Condit Dam is breached in late October. 
7.1.1 This teletype was updated on 15 September to operate to a minimum elevation of 74.0 feet. Therefore, the hard constraint maximum is 75.5 feet and soft constraint maximum is 75.0 feet. This update of the operating range was requested by the Yakama Nation in response to new information regarding the clean-up event at the mouth of the White Salmon river on 17 September. Event personnel have identified that a pool lower than 74.0 feet would prevent boat access to certain areas of the White Salmon river.
7.2 A teletype sent on 09 September requests that BON pool be operated as follows for treaty fishing: Operate within a 1.5’ band, hard constraint from 0600 hours Monday 12 September – 1800 hours 16 September, 2011 during treaty fishing. Steady night time operations are most important (1900 through 0700 hours). A higher pool also facilitates the fishing operations. 
7.2.1 This teletype was updated on 15 September. The update requests to operate to a maximum elevation of 74.8 feet and minimum elevation of 73.3 feet, hard constraint on Friday 16 September, from 0900 to 1400 hours. Target elevation is 74.5 feet. This is to facilitate a fish salvage operation in the White Salmon river. USFWS requested to maintain a minimum pool elevation so that boats can safely implement fish salvage operations downstream of Condit dam. The salvage operation will capture adult fall Chinook so that they can be relocated upstream to spawn above Condit dam.
7.3 A teletype sent on 16 September requests that BON pool be operated as follows for treaty fishing: Operate within a 1.5’ band, hard constraint for the period and time as listed: 0600 hours Monday 19 September to 1800 hours Friday 23 September 2011.
7.4 A teletype sent 16 September states that emergency repair at the B branch Bradford Island fish ladder entrance is required immediately due to structural integrity issues and a high risk of failure related to erosion. The B branch needs to be dewatered and repaired. This Saturday in the morning, both A and B branch will be out of service in order to install concrete orifice blocks in B branch just below the junction pool. Once installed, the A branch will be reopened. Effective immediately and until the fish biologists notify the control room operator operate Powerhouse 2 as priority and then use Powerhouse 1 if additional generation is requested by BPA. Continue with the same unit priority as listed in the 2011 Fish Passage Plan. It is recognized that due to the current high number of adult returning fish the project has been in a split flow unit priority, following the 2011 Fish Passage Plan guidance. Once notified by the biologists, return to this priority unless instructed differently by RCC. Effective immediately stop all attraction flow spill from spillbay 18 and add the same volume on to spill at spillbay 1. Continue this operation until further notice, even after switching back to the split flow gen pattern. The purpose of this operation is to ensure better attraction to the Cascades Island entrance.

JERRY CARROLL
Operations Project Manager
Page 1 of 1
1
Page 2 of 4

