CENWP-OD-B





















30 October 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2011, which covers the period from 23 through 29 October 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 104.3 to 137.7 kcfs.  Daily average project tailwater ranged from 10.0’ to 12.7’ msl.  Daily average powerhouse forebay elevation ranged from 71.6’ to 74.6’ msl.  Daily average river temperature ranged from 58 to 61ºF. Secchi disk measurements ranged from 1.5’ to 7.0’.
1.2 Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 is open 6” during daylight hours per teletype in section 7.2.  Spill bay 18 remains on sill.  Daily average spill ranged from 0.5 to 0.6 kcfs. 
1.3 Unit Operation.  Powerhouse One remains the priority powerhouse.
1.3.1 Unit 9 went out of service at 0728 on 07 September 2011 for bearing replacement.
1.3.2 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.3 Unit 15 went out of service at 0719 on 05 September 2011 due to exciter failure.

1.3.4 Unit 16 went out of service at 0452 on 04 September 2011 due to exciter failure. 

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 F1 went out of service at 0003 on 14 October 2011 for WA shore maintenance.
1.4.2 F2 went out of service at 0005 on 14 October 2011 for WA shore maintenance. 
1.5 Gatewell drawdowns are measured on Tuesdays and more frequently as needed.
2 ACTIVITIES
2.1 Auxiliary Water System Closures.  No AWS closures occurred this reporting week.
2.2 STS/VBS inspections.  No STS/VBS inspection occurred this reporting week. 
2.2.1 Table 1.  STS and VBS inspection.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	STSs scheduled to be pulled starting 31 October.


2.3 Dewatering and Fish Salvage. The following activities occurred this reporting week.
2.3.1 On 28 and 29 October Project Fisheries salvaged 20 White sturgeon, 2 bass, and 1 walleye from Unit 9 tail logs. Fish were released in good condition at the Hamilton Island boat launch.

3 RESEARCH  
3.1 Battelle - survival study.  Monitoring University of Idaho acoustic tagged adult lamprey.  
3.2 CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.  
3.3 NOAA/PSMFC - lamprey.  LPS count network improvements moving forward. 
3.4 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Fallbacks recorded crossing the separator bars: 3 salmon, and 1 unknown salmonid. The JMF is scheduled to go to bypass on 31 October. 
3.5 WDFW - Fish Counting.  Visual counting continues and is scheduled to conclude on 31 October.
4 FISHWAYS 
4.1 Project biologists inspected 23 through 29 October. NOAA inspected on 28 October.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	10/24-27
	A-branch staff gauge
	Out of criteria
	B-branch OOS
	N/A
	

	All week
	BI staff gauge
	Water level < 0.9’
	B-branch OOS
	N/A
	

	All week
	B-branch dewatered
	Emergency repairs
	N/A
	

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS)

	All week
	Ladder dewatered from UMT confluence “Y” junction to TW
	Emergency repairs
	N/A
	


4.2.1 PH1CC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
4.2.3 The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work replacing the PLC to allow for fully automated operation of the PH2 adult fishway is complete but some testing and adjustments are ongoing.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	10/23
	59.8
	60.0

	10/24
	59.3
	59.5

	10/25
	58.6
	58.9

	10/26
	57.7
	58.0

	10/27
	57.3
	57.6

	10/28
	56.7
	57.0

	10/29
	57.0
	57.3


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 21 October.
4.5.2 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance. 
4.5.3 SLEDs were removed from all entrance gates as of 05 July. 
4.5.4 B-branch remains out of service. See section 7.1 and MFR 110919 BON B-branch emergency dewater for more information.
4.5.5 The AFF remains out of service for WA shore repairs.

4.5.6 WA shore ladder remains out of service from the “Y” junction (UMT confluence) to tailwater in facilitation of diffuser grating and AWS repairs. 
4.5.7 The south monolith at PH2 was dewatered on 20 October to facilitate repairs on the B diffusers in anticipation of dewatering the south AWS.

4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service. Submersible Traveling Screens (STSs) are scheduled to be removed starting 31 October.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.
4.6.3 The hydrocannon was returned to service on 06 July.  
4.6.4 The B2CC was closed 01 September.  All B2CC and Cascades Island avian lines were removed to facilitate barge access for B-branch emergency repairs. They will be reinstalled once repairs are complete.
4.6.5 Spill ended on 01 September.
4.6.6 Truck releases of summer out-migrants originating from McNary began on 03 August. Truck releases from Lower Granite, Little Goose and Lower Monumental dams commenced on 17 August. The last Walla Walla District trucking operation is scheduled for 01 November.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.
4.7.2 The CI LPS remains out of service for the season.
4.7.3  The NDE ramp remains out of service for the season.
4.7.4 WA Shore and Bradford Island LPSs remain watered up.
5 CONSTRUCTION
5.1 PH1 Gantry 4. Testing of the new crane continues. Scheduled to return to service week of 31 October.
5.2 B2CC Hoist. Construction scheduled to begin fall of 2011.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER INCESSANT ITEMS
7.1 A teletype sent 16 September states that emergency repair at the B branch Bradford Island fish ladder entrance is required immediately due to structural integrity issues and a high risk of failure related to erosion. Effective immediately stop all attraction flow spill from spillbay 18. Continue this operation until further notice. 

7.2 A teletype sent on 27 September states that, effective immediately operate attraction flow consistent with the 2011 FPP. Specifically, operate spillbay 1 spill gate with an opening of 6 inches. Keep spill gate 18 closed since B-branch is out of service. In the event hydraulic capacity would cause BON to spill then pick up generation at PH1 to Best Geometry prior to spilling at BON. Should spill occur at BON then spill in accordance with the spill pattern titled “Special Spill Pattern for North End Spill Bays 1-9”.
7.2.1 This teletype was updated on 07 October, stating that effective at 0700 hours 11 October, until further notice, change powerhouse priority to PH1. Concurrent with the above operation, operate PH1 turbine units to Best Geometry, expanding the upper limit of the 1% operating range up to 11.7 kcfs per unit. These operations are necessary to reduce flow to PH2 to minimize attraction flow at Washington Shore fish ladder.

7.2.2 This teletype was updated 27 October, stating that effective immediately operate PH1 up to the maximum load within the cavitation limit. If flows exceed PH1 capacity, operate available PH2 units in the following priority: 11, 12, 13, 14, 15, 16, 17, 18.
7.3 A teletype sent on 05 October requests that from 0630 hours on 06 October to 1800 hours 31 October 2011, BPA notify the BON operator and RCC at least 30 minutes, or more, prior to any spill at BON. When notified, BON will take appropriate steps to evacuate workers from the spillway tailrace. When workers are not present, notice may allow the contractor to better secure and monitor equipment in the tailrace before and during spill.
7.4 A teletype sent on 20 October states that, effective at 0600 hours on 21 October until further notice, operate the BON forebay to a minimum elevation of 73.0’ as a hard constraint. Continue with a maximum 75.5’ hard constraint. If spill in necessary, open the Powerhouse 2 Corner Collector to minimize spill. Change in minimum forebay elevations is in response to water depth issues in the A-branch ladder which is currently dependent on forebay elevation for flow due to repair work in B-branch. Forebay elevations below 73.0’ may delay fish passage over the upper A-branch ladder weirs.
7.4.1 This teletype was updated on 24 October to change forebay hard constraint range to 74.5’-75.5’ during daytime hours.
7.4.2 This teletype was updated on 25 October to request that from 0800 hours on 26 October through 1700 hours on 28 October operate forebay within the 71.5’-73.0’ range as a hard constraint to minimize sediment released from the breach of Condit dam.

7.4.3 This teletype was updated on 27 October to cancel the forebay constraints as sediment loads from the breach had decreased and return to the 74.5’-75.5’ hard constraint range during daylight hours.

7.4.4 This teletype was updated on 28 October to change forebay hard constraint range to 73.5’-75.5’ during daytime hours with supplemental flow from Fish Valve 3-9 as needed to maintain approximate criteria in A-branch.

7.5 A teletype sent on 24 October requests that BON tailwater be maintained at or above 11.0’ as a hard constraint from 0700 to 0900 hours on 25 October for transit of a barge to B-branch ladder construction site.

7.6 A teletype sent on 28 October requests that BON tailwater be maintained at or below 10’ as a hard constraint on 30 and 31 October for grout application over new riprap at B-branch site.
JERRY CARROLL
Operations Project Manager
Page 1 of 4
1
Page 4 of 4

