CENWP-OD-B





















20 November 2011
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 46 of 2011, which covers the period from 13 through 19 November 2011.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 122.1 to 146.5 kcfs.  Daily average project tailwater ranged from 11.7’ to 13.3’ msl.  Daily average powerhouse forebay elevation ranged from 73.4’ to 74.1’ msl.  Daily average river temperature ranged from 50 to 54ºF. Secchi disk measurements ranged from 4.0’ to 6.0’.
1.2 Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 remains 12” open during daylight hours.  Spill bay 18 remains on sill.  Daily average spill ranged from 1.0 to 1.3 kcfs. 
1.3 Unit Operation.  Powerhouse One remains the priority powerhouse.
1.3.1 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.2 Unit 15 went out of service at 0719 on 05 September 2011 due to exciter failure. It was returned to service at 1537 on 17 November.
1.3.3 Unit 16 went out of service at 0452 on 04 September 2011 due to exciter failure. 

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 F1 went out of service at 0003 on 14 October 2011 for WA shore maintenance.
1.4.2 F2 went out of service at 0005 on 14 October 2011 for WA shore maintenance. 
1.5 Gatewell drawdowns are measured on Tuesdays and more frequently as needed.
2 ACTIVITIES
2.1 Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.
2.1.1 FV 5-9 was closed for cleaning from 0830 until 0844 on 17 November.
2.1.2 FV 6-9 was closed for cleaning from 0830 until 0844 on 17 November.
2.2 STS/VBS inspections.  No STS/VBS inspection occurred this reporting week. 
2.2.1 Table 1.  STS and VBS inspection.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	STSs removed.


2.3 Dewatering and Fish Salvage. The following activities occurred this reporting week.
2.3.1 On 16 November Project Fisheries salvaged 1 small mouth bass and 1 catfish from unit 15 tail logs. The fish were released into the tailrace in excellent condition.

3 RESEARCH    
3.1 WDFW - Fish Counting.  Video counting continues.
4 FISHWAYS 
4.1 Project biologists inspected 13 through 19 November.
4.2 Fish Passage Plan Observations.
Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	BRADFORD ISLAND (BI)

	11/15-17
	A-branch staff gauge
	Water level > 1.1’
	B-branch OOS
	N/A
	

	All week
	BI staff gauge
	Water level < 0.9’
	B-branch OOS
	N/A
	

	All week
	B-branch dewatered
	Emergency repairs
	N/A
	

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS)

	All week
	Ladder dewatered from UMT confluence “Y” junction to TW
	Emergency repairs
	N/A
	

	All week
	DSM2 dewatered
	Emergency WA shore repairs
	N/A
	


4.2.1 PH1CC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.  

4.2.2 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
4.2.3 The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work replacing the PLC to allow for fully automated operation of the PH2 adult fishway is complete but some testing and adjustments are ongoing.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November.
Table 3.  Bonneville Fishway Temperatures

	Date
	WA. Shore average
	BI

average

	11/13
	51.7
	51.9

	11/14
	51.1
	51.4

	11/15
	50.6
	50.9

	11/16
	50.0
	50.2

	11/17
	49.2
	49.6

	11/18
	48.9
	49.2

	11/19
	48.8
	49.1


4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 18 November.
4.5.2 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance. 
4.5.3 SLEDs were removed from all entrance gates as of 05 July. 
4.5.4 B-branch remains out of service. 
4.5.5 The AFF remains out of service for WA shore repairs.

4.5.6 WA shore ladder remains out of service below the “Y” junction (UMT confluence) in facilitation of diffuser grating and AWS repairs. 
4.6 Juvenile Fishways.
4.6.1 DSM2 remains out of service. STSs are removed.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.
4.6.3 The hydrocannon remains winterized.  
4.6.4 The B2CC remains closed.  All B2CC and Cascades Island avian lines were removed to facilitate barge access for B-branch emergency repairs. They will be reinstalled once repairs are complete.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.
4.7.2 All LPS systems remain out of service for the season.
5 CONSTRUCTION
5.1 B2CC Hoist. Construction has begun and will continue throughout the winter.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS
7.1 A teletype sent on 31 October states, effective 01 November operate BON tailwater to provide adequate spawning conditions for Chum salmon. Hard constraint 1: Maintain tailwater at a minimum of 11.3’ all hours. Hard constraint 2: Maintain tailwater within 0.7’ band of 11.3’-12.0’ daily from 0630-1700 hours.

7.2 A teletype sent on 10 November updated and replaced previous teletypes concerning forebay range, PH priority, and spill operations.
7.2.1 Continue to operate BON forebay in the 73.0-75.5’ range during daytime hours. FV 3-9 may be operated to provide additional water to A-branch as necessary.
7.2.2 Continue to operate PH1 as the priority powerhouse, and operate the units up to the cavitation limit.
7.2.3 Continue to open spill bay 1 12” during daytime hours to provide additional attraction flow to Cascades Island. Keep spill bay 18 on sill.
7.2.4 Effective immediately until 1700 hours on 13 November spill flows in excess of PH1 capacity with the spill pattern titled “Special Spill Pattern for North End Spill Bays 1-9” up to 70 kcfs during daytime hours. Operate PH2 units for flows in excess of PH1 capacity during nighttime hours. After 1700 hours on 13 November operate PH2 units for flows in excess of PH1 capacity for all hours.
7.3 A teletype sent on 17 November states that, effective immediately, change PH2 unit priority to: 15, 12, 13, 14, 16, 17, 18. This operation is necessary to run heat tests on unit 15 prior to returning the unit to service.
JERRY CARROLL
Operations Project Manager
Page 1 of 1
1
Page 2 of 3

