CENWP-OD-B





















08 April 2012
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 14 of 2012, which covers the period from 01 through 07 April 2012.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 283.4 to 346.9 kcfs.  Daily average project tailwater ranged from 23.5’ to 26.4’ msl.  Daily average powerhouse forebay elevation ranged from 72.4’ to 75.4’ msl.  Daily average river temperature ranged from 44 to 45ºF. Secchi disk measurements ranged from 2.5’ to 5.0’.
1.2 Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bays remain 6” open during daylight hours. Daily average spill ranged from 74.6 to 136.5 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse.
1.3.1 Unit 1 was out of service from 0856 until 0918 and from 1241 until 1354 on 03 April to rake trash.

1.3.2 Unit 7 was out of service from 1356 until 1644 on 03 April, and from 0653 until 0745 on 04 April to rake trash.

1.3.3 Unit 10 was out of service from 0750 until 1133 on 04 April to rake trash.
1.3.4 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.5 Unit 12 was out of service from 0654 until 1107 on 03 April for exciter monitoring equipment installation. Unit 12 was also out of service from 1443 until 1537 to connect WEC testing equipment and from 1602 until 1606 for testing WEC on 05 April.
1.3.6 Unit 13 was out of service from 1111 until 1400 on 03 April for an exciter test point installation.
1.3.7 Unit 14 was out of service from 1402 until 1617 on 03 April for an exciter test point installation.
1.3.8 Unit 15 was out of service from 1750 until 1825 on 02 April due breaker misoperation at the BPA substation. Unit 15 was also out of service from 0653 until 1109 on 04 April for exciter monitoring equipment installation
1.3.9 Unit 16 was out of service from 1750 until 1826 on 02 April due breaker misoperation at the BPA substation.

1.3.10 Unit 17 was out of service from 1750 until 1822 on 02 April due breaker misoperation at the BPA substation. Unit 17 was also out of service from 1109 until 1558 on 04 April for an exciter test point installation.
1.3.11 Unit 18 was out of service from 1750 until 1822 on 02 April due breaker misoperation at the BPA substation.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 Fish Unit 2 was out of service from 1750 until 1833 on 02 April due breaker misoperation at the BPA substation.

1.5 Gatewell drawdowns are measured on Tuesdays and more frequently as needed.
2 ACTIVITIES
2.1 Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.
2.1.1 FV 1-1 was closed to float trash from 2146 until 2155 on 04 April.
2.1.2 FV 3-7 was closed for cleaning from 1009 until 1055 on 02 April.

2.1.3 FV 5-9 was closed for cleaning from 1059 until 1106 on 02 April.

2.1.4 FV 6-9 was closed for cleaning from 1108 until 1112 on 02 April.
2.2 STS/VBS inspections.  No STS/VBS inspection occurred this reporting week. 
2.2.1 Table 1.  STS and VBS inspection.  

	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for week of 08 April


2.3 Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this week.
3 RESEARCH    
3.1 Battelle - survival study.  Surgeon/tagging training and fish condition research continue at the JMF. Fish for training currently held in raceways at the SMF. Hydrophone installation completed on 21 March.
3.2 CRITFC - Sea lion hazing.  Hazing from boats began on 05 March.
3.3 FFU - Sea lion.  Observations continue. Weekly pinniped reports can be found at: http://www.nwd-wc.usace.army.mil/tmt/documents/fish/2012/sea_lion_hazing2012.html
3.4 ODFW/WDFW - Sea lion. Sea lion traps remain adjacent to the B2CC and downstream of the old Navlock.  Acoustic tagging and branding began on 06 February. NOAA Fisheries authorized permanent removal of specific California sea lions effective 20 March. 
3.5 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring began on 01 March. Sort by Code is active. Fallbacks recorded crossing the separator bars this week: 13 steelhead and 2 unknown salmonid. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm
3.6 USDA - Sea lion hazing. Hazing from the deck began on 01 March.
3.7 WDFW - Fish Counting.  Visual counting began on 01 April.
4 FISHWAYS 
4.1 Project biologists inspected 01 through 07 April.
4.2 Fish Passage Plan Observations.
4.2.1 Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE
	TR#

	SPILLWAY

	All week
	Bay 11
	On sill
	Failed hoist
	None
	N/A

	BRADFORD ISLAND (BI)

	04/07
	PH1CC
	N and S differentials > 2.0’
	Unknown
	None
	N/A

	04/07
	SCH velocity
	Velocity < 1.5 fps
	Unknown
	None
	N/A

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS) – Nothing to report.


4.2.2 PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.  

4.2.3 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November. Temperatures are unavailable this week due to technical difficulties.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 07 April.
4.5.2 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance. Sea lion barriers are in place on all installed FOGs.
4.5.3 All SLEDs are installed.
4.5.4 All ladders remain in service.

4.5.5 The AFF remains dewatered. It is scheduled to be watered-up on 11 April.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto. 
4.6.3 The hydrocannon remains in service.  
4.6.4 The B2CC was opened on 19 March upon reaching the kelt trigger.
4.6.5 All B2CC and Spillway avian lines were removed to facilitate barge access for B-branch emergency repairs. The spillway array was reinstalled on 27 and 28 March.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.
4.7.2 All LPS systems remain out of service for the season.
5 CONSTRUCTION
5.1 B2CC Hoist. Construction is complete. Final testing and modifications continue.
5.2 Seawater Recirculation System Removal (JMF). Removal continues.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES AND OTHER NOTEWORTHY ITEMS

7.1 A teletype sent on 23 November states in order to keep the latest established Bon tailwater flow range for chum, total project flow may be decreased to as low as 58 kcfs as long as the estimated flow at the confluence of the Columbia and Willamette rivers is equal to or exceeds 77 kcfs.  The 58 kcfs and 77 kcfs is a hard constraint navigation requirement.  

7.2 A teletype sent on 28 December replaces a previous teletype for operation of BON tailwater to provide adequate spawning conditions for Chum salmon. As a hard constraint, maintain tailwater at a minimum of 12.0’ all hours.
7.3 A teletype sent on 04 April updates the spill priority list order for Fish Passage Season for the Columbia Basin projects with associated total dissolved gas spill caps.

7.4 A teletype sent on 06 April requests that, as a soft constraint, the BON forebay be at or below elevation 72.5’ from 1200 until 1500 hours on 09 April. The requested operation assists contractors welding together 15 steel pilings to from three dolphins for the city of The Dalles.

JERRY CARROLL
Operations Project Manager
Page 1 of 1
1
Page 2 of 3

