CENWP-OD-B





















20 May 2012
MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist
SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 20 of 2012, which covers the period from 13 through 19 May 2012.
1 OPERATION SUMMARY

1.1 Daily average river flows ranged from 308.2 to 391.2 kcfs.  Daily average project tailwater ranged from 23.1’ to 26.8’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 75.4’ msl.  Daily average river temperature ranged from 54 to 56ºF. Secchi disk measurements ranged from 2.4’ to 4.0’.
1.2 Spring Spill for fish passage is in effect until 15 June. Daily average spill ranged from 101.2 to 155.5 kcfs.
1.3 Unit Operation.  Powerhouse Two is the priority powerhouse.
1.3.1 Unit 7 was out of service from 0012 on 14 May until 0900 on 17 May for annual maintenance.

1.3.2 Unit 8 was out of service from 0121 on 07 May until 1129 on 10 May for an annual overhaul.

1.3.3 Unit 11 has remained out of service since 12 June 2008 due to rotor damage.
1.3.4 Unit 12 was out of service from 1005 until 1131 on 16 May for governor control oil regulator work.

1.3.5 Unit 18 was out of service from 0049 on 12 May until 1356 on 15 May for an oil leak in governor piping.
1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris. 
1.4.1 Fish Units 1 and 2 were out of service from 1914 until 2054 on 07 May to float trash.

1.5 Gatewell drawdowns are measured on Tuesdays and more frequently as needed.
2 ACTIVITIES
2.1 Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.
2.1.1 FV1-1 was closed from 2330 on 15 May until 0430 on 16 May and from 2245 on 17 May until 0355 on 18 May for cleaning.
2.2 STS/VBS inspections.  No STS/VBS inspection occurred this reporting week. 
2.2.1 Table 1.  STS and VBS inspection.  
	Unit
	Date
	Run Hours
	Comments

	11
	NA
	OOS
	U11 remains out of service.

	12-18
	NA
	NA
	Inspection scheduled for week of 21 May


2.3 Dewatering and Fish Salvage. The following dewatering or fish salvage activity occurred this week.
2.3.1 On 16 May fisheries personnel recovered 19 Sturgeon, and 3 adult Chinook from the Unit 11 draft tube. All fishes were released upstream in good condition.
3 RESEARCH
3.1 Battelle/PNNL – Surgeon Training/Assessment. Surgeon assessment and Sort-By-Code activities will continue through July.
3.2 Battelle/PNNL - Survival Study. Hydrophones remain installed.
3.3 CRITFC – AFF.  Annual Chinook, Coho, Sockeye and Steelhead sampling in the AFF began 23 April.
3.4 CRITFC - Sea Lion Hazing.  Hazing continues.
3.5 FFU - Sea Lion.  Observations continue. Weekly pinniped reports can be found at: http://www.nwd-wc.usace.army.mil/tmt/documents/fish/2012/sea_lion_hazing2012.html
3.6 NOAA – Juvenile Steelhead. Barged and in-river migrant sampling began 03 May.
3.7 NOAA - Lamprey. Personnel moved the lamprey trap davit at the South Monolith SDE closer to the entrance allowing the trap to sit adjacent to attraction flow. LPS count network installation continues.
3.8 NOAA – Pathology. 25 yearling Chinook and 25 Coho were collected at the JMF for research this week.
3.9 ODFW/WDFW - Sea lion. Sea lion traps remain downstream of the old Navlock. Two traps were moved to the forebay, upstream of the old Navlock in an effort to capture the sea lions above Bonneville.  Acoustic tagging and branding began on 06 February. NOAA Fisheries authorized permanent removal of specific California sea lions effective 20 March. 
3.10 PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Sort by Code is active for PNNL and NOAA. Fallbacks recorded crossing the separator bars this week: 58 steelhead, 25 salmon, and 32 unknown salmonids. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details. 
3.11 USDA - Sea Lion/Avian hazing. Hazing continues.
3.12 WDFW - Fish Counting.  Visual counting continues.
4 FISHWAYS 
4.1 Project biologists inspected 13 through 19 May.
4.2 Fish Passage Plan Observations.
4.2.1 Table 2.  FPP Out of Criteria items.
	DATE
	LOCATion
	FPP itEMS
	CAUSE
	RESPONSE

	SPILLWAY

	All week
	Bay 17
	Incorrect height for spill pattern
	Failed hoists
	Under repair

	BRADFORD ISLAND (BI) – Nothing to report.

	CASCADES ISLAND (CI) – Nothing to report.

	WASHINGTON SHORE (WS)

	All week
	PH2 Entrances
	Gates < 13’ submergence
	Necessary to maintain differential
	N/A


4.2.2 PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.  

4.2.3 A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.
4.3 Fishway Temperatures.  Temperatures are taken 01 March through 30 November. Temperatures are unavailable this week due to technical difficulties.
4.4 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.  
4.5 Adult Fishways. 
4.5.1 Calibration was checked on 19 May.
4.5.2 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance. Sea lion barriers are in place on all installed FOGs.
4.5.3 All SLEDs are installed.
4.5.4 All ladders remain in service.

4.5.5 The AFF remains in service.
4.6 Juvenile Fishways.
4.6.1 DSM2 remains in service.
4.6.2 The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto. 
4.6.3 The hydrocannon remains in service.  
4.6.4 The B2CC remains open.
4.6.5 The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2013.
4.7 Lamprey Fishways.
4.7.1 The Cascades Is. entrance weir remains installed.
4.7.2 All LPS systems remain out of service. They are scheduled to return to service in mid May.
5 CONSTRUCTION
5.1 Seawater Recirculation System Removal (JMF). Removal continues.
6 HAZMAT, SPILLS AND CLEANUP. Nothing to report.
7 TELETYPES CURRENTLY IN EFFECT
7.1 A teletype sent on 09 April states that, effective from 0001 hours on 10 April until 2400 hours on 15 June, operate in accordance with the 2012 Fish Operations Plan to provide spill for juvenile fish passage during the spring season at BON, as follows: 100 kcfs for 24 hours per day following the spill pattern defined in the 2012 Fish Passage Plan. This teletype was updated on 20 April to define minimum generation requirements.
7.2 A teletype sent on 18 May updates the spill priority list order for Fish Passage Season for BON with associated total dissolved gas spill caps.
7.3 A teletype sent on 11 May states that, effective through 18 May, for the purposes of system flood control; make best efforts to keep BON max instantaneous flow no higher than 420 kcfs.

7.4 A teletype sent on 16 May states that effective immediately through 1800 hours on 21 May, operate to move flow that would normally pass through PH2 units above the midpoint (50%) of the 1% operating range to pass instead through PH1 units operating above the 1% range to the best geometry point. This operation is intended to improve passage conditions through PH2 gatewells during the downstream migration of Sockeye salmon.
JERRY CARROLL
Operations Project Manager
Page 1 of 3
1
Page 3 of 3

