U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#28-2008
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  September 5 - 11, 2008
Turbine Operation

McNary had 11 to12 turbine units available for power generation this week.  Major outages included turbine unit 5 (9-year overhaul, expected return to service is next week) and turbine unit 8 (annual maintenance and external thrust bearing oil cooler work).  Eight turbine outages were necessary this week as divers removed USGS research equipment.  Individual dive outages included turbine unit 1 (September 8 and 9), turbine units 2, 4, and 6 (September 9, combined outage time 7.6 hours), turbine units 9 – 14 (September 10, combined outage time 24.6 hours), and turbine units 13 and 14 (September 11, 18.4 hours combined outage time).  Other outages affected turbine unit 2 on September 10 and 11 (respective outage times and reasons are: 1 hour, 3D cam alarm and 2 hours, low turbine bearing oil alarm), turbine unit 9 (September 10 and 11, fuse problem) and turbine unit 11 (September 6, thrust bearing cooling drain line repair, 2.3 hours outage time).  Although no turbine units operated outside the 1% criteria this week, turbine units 2 and 9 were restricted to operations at the lower end of the 1% criteria on September 10 and 11 due to high VBS differential readings.

Adult Fish Passage Facilities

On September 6, 8 and 11, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting continues.  Temperature monitoring at the ladder exits will conclude September 15.                            
Fish Ladders:  Both ladders met all Fish Passage Plan criteria except on September 8 when the Oregon ladder count station differential was 0.7 feet due to debris on the picketed leads.  Criteria was met after the leads were cleaned the same day.  The north Oregon ladder traveling screen remains out of service and work continues toward resolution of this issue.  The south traveling screen has been operating well.  Both ladders exit set points were check twice this week and no changes were noted.      

Fishway Entrances and Collection Channel:  Fish entrance and ladder passage remains strong.  The Washington ladder met all criteria points even though project personnel noted that W2, though in criteria, required calibration.  Oregon entrances and collection channel inspection points met criteria except for the north powerhouse entrance (pool differential was 0.8’ on September 11) and  NFEW2 and NFEW3 (both measured 8.6 to 8.9’ weir depths all week).  The channel velocity averaged 1.3 feet per second.  
Auxiliary Water Supply System:  With fish pump 3 out of service until the winter maintenance season due to an oil leak, pumps 1 and 2 ran all week with blade angles of 30 degrees.  The juvenile facility continued to supply the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no service interruptions this week.   
Juvenile Fish Passage Facility

Collection for truck transport continued.  Primary bypass operations became necessary on 3 occasions this week.  Two of these occurrences (September 5, 0000 – 0200 hours and September 7-8, 2200 – 0200 hours) were due to influxes of juvenile shad.  Primary bypass is sometimes necessary during night hours when juvenile shad out-migrate in larger numbers.  Too many shad in the fish trailer can block circulation screens.  The remaining bypass operation took place September 5 from approximately 0700 hours to 1050 hours after facility personnel noticed that the B-side sample gate actuator had failed.  The gate was in the raceway position (sample gate closed) when the failure occurred.  Collection resumed after a replacement actuator was prepared and installed.  For the report week, 5,015 smolts and 172,545 juvenile shad were collected and trucked down river.                              

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was very light to light.  No trash racks were cleaned and differentials continued to be monitored.  No problems were observed within the gatewell slots.  On September 11, the emergency bulkhead was removed from 5B slot.                                 

ESBSs/VBSs:  ESBSs are currently deployed in all turbine unit slots except for those in slots 5B and 5C.  One screen is still undergoing maintenance and the other is being kept in reserve as a spare as turbine unit 5 is out of service.  These screens are slated to be reinstalled next week.  Fish screens in slots 4B and 11C slots remain in transducer bypass mode.  No ESBS problems were encountered this week other than cable adjustments for the screens in slots 3A and 3B.  ESBS camera inspections will resume when a new camera cable is ordered and installed.  Three high VBS differentials were recorded on September 10 when turbine units were operating at 60 megawatts.  These screens and one other screen were cleaned the next day.                                                  

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  During the week, 40 to 42 orifices were opened depending on forebay elevation.  All turbine unit 5 orifices were closed as the turbine unit and associated ESBSs were out of service.  Additional orifices were opened in adjacent turbine units to maintain proper collection channel elevation.   Once the ESBSs are reinstalled in slots 5A and 5B, these orifices will be reopened.  All systems functioned well this week.                  

Transportation Facility:  Collection for truck transport continued.   PIT tag detection took place in the full flow pipe and throughout the facility with smolt monitoring occurring daily.  All systems functioned well except the broken B-side sample gate actuator mentioned above, and replacement of a leaking air hose at the B-side sample gate on September 10 (sampling operations were not interrupted).  The primary (A and B) PIT tag slide gates remained on, and the secondary (C and D) PIT/bypass gates were closed (off for duration of transport operations).  These gates underwent scheduled testing on September 10.  Balloon test of the PIT tag release lines revealed no problems (project personnel release balloons filled with air and water into the PIT tag lines – if intact balloons are observed exiting the outfall, there are no blockages).  When sampling at rates of 20 percent or higher, PIT tag diversion gates are set to override the sample gates.

Transport Summary:  Truck loading occurred on September 6, 8 and 10.  No problems were encountered this week.      

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff with the data day running from 0700 to 0700 hours.  During the week, the spill gates underwent scheduled maintenance.    

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	118.6
	75.7
	0.0
	0.0
	67.9
	66.3
	6.0
	     6.0


*Morning wet lab temperature.  Water clarity provided by control room.

Other

Bird counts continued with the tailwater being checked twice a day and the forebay once per day.  The high count in the tailrace area was approximately 60 gulls and 34 cormorants with an occasional pelican or tern being noted.  No birds were seen by the bypass outfalls.  The water cannon continues to be operational as PIT tagged fish are exiting one of the outfalls.  In the forebay area, only an occasional grebe was noted and no grebes were observed in the gatewell slots in or the juvenile collection system.  Bird numbers on project appear to fluctuate significantly and probably are affected by out migrating juvenile shad numbers.  Most research studies have concluded for the season.  

Project:  Ice Harbor

Biologist:  Mark Plummer

Dates:  September 5 - 11, 2008

Turbine Operation

Turbine units 1, 2, and 6 were available for operation through the entire reporting period. Turbine units 2 and 3 respectively went out of service September 8 at 0738 hours and 0805 hours for cooling water strainer replacement.  Turbines 2 and 3 share a common cooling water intake strainer.  Turbine unit 4 was out of service from September 8 (0930 hours) to September 11 (1215 hours) in support of Doble testing.

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways September 2, 3, and 4.
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.     
Fishway Entrances and Collection Channel (in inspection date order):  The south shore entrance (SFE) was on sill with a depth of 7.9 feet, on sill with a depth of 8.2 feet, and on sill with a depth of 6.4 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.9 feet, on sill with a depth of 8.2 feet, and on sill with a depth of 6.4 feet.  The north shore entrance (NSE) was off sill with a depth of 7.9 feet, off sill with a depth of 8.1 feet, and on sill with a depth of 6.4 feet.   Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were within criteria (differential criteria are 1 – 2 feet).  
Auxiliary Water Supply System:  2 of the 3 north fish pumps and all eight south shore fish pumps were operated without problems.  North shore fish pump 2 remains out of service.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.  

STSs/VBSs:  STSs were placed in cycle run mode on August 14 as subyearling Chinook lengths exceed 120 mm in length at Lower Monumental Dam.  No problems were found during the August STS inspections.  Turbine units 1, 2, 3, and 4 STSs were inspected while these units were out of service.  The screen in turbine unit 3, slot C was found to be inoperative (i.e: not turning).  The screen was raised and repairs are in progress.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   20 orifices are open.    No problems to report.
Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.  270 cfs is dewatered and directed into the south adult fish pump chamber for additional adult fish attraction water.    

Removable Spillway Weir:  RSW operation ceased with the end of summer spill for fish August 31.  

Fish Sampling:  Juvenile fish sampling concluded July 31.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	36.9
	16.5
	0.0
	0.0
	69.0
	69.0
	6.8


	6.8


*Unit 1 scrollcase temperature.

Other

Gatewells in turbine units 2 and 3 were dipped for fish prior to bulkhead placements and dewatering.  Gatewell slots 2A and 3A were respectively dipped on September 8 and 11 prior to being unwatered in support of cooling water strainer replacement.  Approximately 300 juvenile shad were captured and released into the adjoining gatewell slots.  No salmonids were observed.
Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Ken Fone 

Dates:  September 5 - 11, 2008

Turbine Operation

Since April 1, all turbine units are being operated in hard constraint of the 1% operation criteria.  Turbine units were taken out of service one at a time for STS inspections on September 8 and 10.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on September 6 and 10. 

Fish Ladders: 

Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively).  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The upper south ladder diffuser was changed to manual control when automatic controls failed.  A trouble report has been submitted.
Fishway Entrances and Collection Channel:  

NSE1 and NSE2 weir gates were in depth criteria (criteria: > 8’ or on sill) throughout this reporting period.  North shore channel/tailwater head was in criteria (1’-2’).  
SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’, on sill, or closed during 2-pump operation) throughout this period with depths from 6.1 to 6.4 feet.    South powerhouse channel/tailwater head was within criteria (1’-2’).    

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) through this period with depths from 7.0 to 7.6 feet.  SSE2 was in criteria (6’ above sill).  South shore channel/tailwater head was in criteria (1’-2’) feet.  

Auxiliary Water Supply System:

Auxiliary water supply pumps 1 and 2 are operating satisfactorily.  Pump 3 is out of service in support of diffuser assembly and bearing housing repairs.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.  Two-pump operation is expected to continue for the remainder of this operating year.   
Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 0.0 square yards of forebay debris observed during this period.  There was 0 - 4% debris coverage in the gatewells.   No oil was observed.     

STSs/VBSs:  STS operation was changed to cycle mode on August 2 when an average fork length of greater than 120 mm was seen in sub-yearling chinook.   STS inspections occurred on September 8, and 10.   No problems were discovered.
Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass is operating with 19 orifices open.  
Collection Facility:  No problems.
Transport Summary:   Alternate day midi-tank truck transport began on August 17.  

A 2.4 milligram per liter (6# to 300 gallon) salt solution was used on all trips to treat and/or ease suspected outbreaks of Flexibacter columnaris.
River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	36.8
	21.5
	0
	0
	66
	65
	5+
	3.7


   *Scrollcase temperatures.

Other

Zebra mussel monitoring stations were checked on September 3 and no mussels were found.

Project:  Little Goose

Biologists:  Eric Volkman and George Melanson

Dates:  September 5 - 11, 2008

Turbine Operation

Turbine units 1, 3, 4 and 5 were available for service during this report period.  Turbine unit 2 remains out of service for annual inspection.  Turbine unit 6 remains out of service due to electrical grounding (water in the stator).  
Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway on September 9, and 11.

Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  All fishway inspection points were in criteria during the report period. Channel to tailwater head differentials during the report periods ranged between 1.20 and 1.60 feet (criteria 1.0 – 2.0 ft.).  SSE weir depths ranged between 8.22 and 8.26 feet (criteria 8.0 ft. minimum).  NPE weirs rested on sill between 5.60 and 5.92 (criteria 7.0 ft minimum or on sill), NSE weir depths ranged between 6.10 and 6.22 feet (criteria 6.0 ft. minimum). Collection channel water velocities (criteria 1.5 – 4.0 fps) held steady at 2.7 fps at the SSE and ranged between 2.4 and 2.6 fps near the NSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.8 and 2.0 fps.  
Auxiliary Water Supply System:  All three fish pumps operated within criteria during the report period.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebey and gatewell debris was minimal this report period. 

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 22 open orifices.  

Extended Length Submersible Bar Screens/Vertical Bar Screens (ESBS/VBS):  All ESBS/VBS operated within criteria during the report period.  Drawdown inspections were conducted on turbine unit slots 1A through 2C, and 4A through 4C on September 8.  All measurements were within criteria.

Transportation Facility:  The facility continued collection for transport operations.  Daily fish smolt collection ranged between 13 and 27 with a total of 138 collected for the week.  Descaling and mortality remained low during the period and averaged 0.3% and 3.9% respectively.

Transport Summary:  Alternate day truck transport operations continued this report period with the 300-gallon midi tank used on September 6, 8 and 10.  Truck loading, transport and release were performed without problems.      
River Conditions

Spill ended 0001 hours on September 1. 

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	Low
	High
	Low
	High
	Low
	High
	Low
	High

	23.6
	34.5
	0
	0
	65.6
	67.0
	5.8
	6.0+


*Ladder temperature.

Other

The University of Idaho continued with adult fish passage research involving tracking of adult salmon and hydrologic flow patterns in the tailrace.  
Piscivorous bird activity continued to be minimal with up to 10 cormorants and 4 gulls observed in the vicinity of the dam during the report period.

Project:  Lower Granite

Biologists:  Mike Halter and Kent Blevins

Dates:  September 5 - 11, 2008

Turbine Operation

Lower Granite had turbine units 1, 4, and 6 available for power generation at the beginning of the report week.  Turbine unit 2 remained out of service for a rewind of the generator and repairs to the blade and liner.  It is projected to return to service September 30, 2008.  Turbine unit 3 is projected to return to service on December 31, 2008 following a 6-yr overhaul. Turbine unit 5 was taken out of service at 0758 hours on September 2 for annual maintenance and a CO2 (fire protection system) upgrade.  It is projected to return to service on September 26.  All operating turbine units were run within the established guidelines.  

Adult Fish Passage Facility

On September 5, 6, 7, and 9 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  
Fish Ladder:  All criteria were met. 
Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during this week’s inspections.  Weir depths at the south shore fishway entrances also met criteria during the week.  The north powerhouse fishway entrance weirs were on sill all week due to tailwater elevations below 636.0 feet (at which level these gates bottom out).  Weir depths at the north powerhouse entrances ranged from 5.9 to 6.2 feet.   North shore fishway entrance weir gate depths were out of criteria all week and varied between 5.5 and 5.7 feet (criteria ≥7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway transition pool ranged from 0.81 to 1.00 feet per second and averaged 0.92 feet per second.

Auxiliary Water Supply System:   Fish pumps 1 and 3 were operated during the week.  
Juvenile Fish Passage Facility
The sample rate remained at the 100% level during the report week.   

Forebay Debris/Gatewell Debris/Oil:   Debris levels were very low in the forebay and gatewells during the week.  There was no evidence of oil in any gatewell.     
ESBSs/VBSs:   Nothing to report.  The next video inspections are scheduled for October.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Collection gallery orifices are being backflushed every 3 hours around the clock to prevent blockages.  It was not necessary to dewater the separator inclined screen to remove debris this week.  
Transportation Facility:   The transport facility operated without any problems.  Debris levels remained low throughout the week.
Transport Summary:  Trucking operations to the release pipe below Bonneville continued during the week.  Due to relatively low fish numbers (and poundage), Lower Granite continued to truck fish using the pickup midi-tanker during the week.
Removable Spillway Weir:   Nothing to report on the RSW.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	37.2
	24.1
	0.0
	0.0
	64.4
	62.9
	5.0
	4.5


*Scrollcase temperature.

Other
The adult fish trap continued operation during the report week.  The sample rate remained at 20%.  Scale samples are being taken off unmarked Chinook and also off both hatchery and wild steelhead.  Tissue samples are also being taken off wild steelhead.

NOAA-Fisheries marking operations to evaluate late season trucking operations continued in the lab.

Fish Facility personnel began cormorant counts in the forebay and tailrace areas of the dam three days per week (morning and evening counts).  This work will continue through the fall months.

COE fisheries technicians began recording data from adult Chinook that “fallback” across the separator for the Washington Department of Wildlife’s Snake River Lab.  Data is being recorded on maturity (adult or jack), hatchery or wild (adipose clip), caudal fin clips, operculum punches, VIE tags, and general fish condition.  This is a continuation of work conducted during the fall months in 2006 and 2007.

An “End of MOP” (minimum operating pool) message was received on September 10.

