U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#22-2009
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  July 24 - 30, 2009

Turbine Operation

McNary had 10 to 11 turbine units available for power generation this week.  Turbine units 7 and 8 remain out of service for replacement of transformer, T4.  This work should be completed in approximately one week.  Turbine unit 2 remains out of service for approximately two months in support of the nine year overhaul.  On July 26, turbine unit 14 was out of service 18 minutes for ESBS camera inspection.  From July 27 to 30, turbine unit 3 was out of service for annual maintenance.  On July 28, turbine unit 11 was out of service 2.5 hours for 3D cam work.  All turbine units operated within the hard one percent criterion except on July 28 when turbine unit 11 ran outside the criteria for five minutes in support of GDAC testing.  On July 29, due to spill closure (in support of fish towboat and barge operations) and high forebay elevations, the powerhouse operated at the upper end of the 1% criteria.  Otherwise, turbine units have been operating at reduced loads with north powerhouse priority for temperature abatement.  

Since July 23, one or two turbine units at the south end of the powerhouse have been temporarily operated in place of one or two turbine units at the north end of the powerhouse whenever the a towboat and fish barge traversed the tailrace to or departed from the juvenile fish facility.  This procedure reduced the intensity of hazardous eddies at the south end of the tailrace.  
On July 24, spill discharge was returned to 50 percent of total flow.  
Adult Fish Passage Facilities

July 26, 27 and 28, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting, annual temperature monitoring and the lamprey passage study continue.  

Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders except on July 27 and 28 when the Washington ladder’s head over weir measured 1.4 feet and the Oregon ladder’s count station differential measured 0.6 feet, respectively.  These reading may have been due to milfoil on the picketed leads or a set point adjustment.  Both exits’ picketed leads and trash racks were cleaned multiple times due to northeast winds occurring during the week.  The Oregon exit alarmed twice this week and was reset.  The Oregon exit’s north traveling screen remains out of service.  The south traveling screen remains in automatic operation, cycling 6 times per day.  Differential monitoring continues.  The screen’s differential did not increase but its trash racks differential went from 1.0 to 1.9 feet.  Measures will be taken to clean the trash rack in the near future.                   

Fishway Entrances and Collection Channel:  All Washington ladder inspection points met criteria.  All Oregon ladder inspection points met criteria except for the north powerhouse pool differential (measured 0.7 to 0.9 feet all week), SFEW1 on July 26 & 27 ( measured 8.8 to 8.9 feet), and SFEW2 on July 27 (measured 8.9 feet).  All other Oregon ladder inspection points were in criteria.  The collection channel velocity averaged 1.7 feet per second.    
Auxiliary Water Supply System:  Although repairs have been completed, fish pump 3 remains out of service.  Maintenance personnel will attempt to place fish pump #3 into operation and place fish pump #1 on standby status in the near future.  Pumps 1 and 2 ran all week with blade angles of 30 degrees.  The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool and the Wasco County PUD unit had no interruptions in service this week.          

Juvenile Fish Passage Facility

Fish collection for daily barge transport commenced July 23, with the first daily barge departure taking place July 24.  Barges being loaded on even numbered days this month begin their trips at Lower Granite Dam.  Barges being loaded on odd numbered days begin their trips at McNary Dam.  USGS researchers completed their fish tagging activities on July 27.  For the report week, 58,460 smolts were collected for transport.  Daily facility mortality rates ranged from 0.5 to 1.8 percent this week. 
Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains very light though some woody debris and Eurasian milfoil persist near the Oregon ladder exit.  Trash rack differentials remained low and no racks were cleaned this week.  No gatewell problems were encountered this week other than slight oil sheens that were removed from 4 slots.  Gatewell slots 7B, 7C, 8A, 8B remain covered to prevent contamination should a spill take place during the course of T4 transformer replacement.  
ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  Screens in slots 11C and 13A remain in transducer bypass mode.  ESBS video camera inspections were conducted in turbine unit 14 this week and no problems were observed.  VBS monitoring revealed no screens out of criteria.  However, 19 VBSs were cleaned as a preventive measure on July 28, 29 and 30.    
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, there were 42 orifices opened.  On July 28, ESBS cables were removed from the orifice inflow in slot 5A.  No other problems were encountered and all automated equipment continued to operated well.  The collection channel was monitored during VBS cleaning.              

Transportation Facility: Collection for barge transport continued.  The primary (A and B) PIT tag diversion gates are in service and the secondary (C and D) PIT/bypass gates remain closed.  Sample gates satisfactorily this week except on 2 occasions.  The sample gates are normally overridden by PIT tag gate operation whenever the sample rate is 20% or greater.  The PIT tag system over ride was left off for one 24 hour sample period when it should have been active (i.e.: sample rate was >20%) and left active for 1 hour on another occasion the over-ride should have been shut off (i.e.:sample rate was < 20%).  Maintenance this week included water balloon tests of the return to the river lines (no ruptured balloons means no obstructions or debris) and additional facility cleaning on a daily basis due to excessive algae growth promoted by the recent warm weather. 
Transport Summary:  Barge departures took place daily from July 24 to 30.  All barges were loaded without incident.  
River Conditions

River conditions during the week are outlined in Table 1 with data provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Water clarity data continues to be provided by the control room.  The smolt monitoring staff continues gathering water temperature data throughout the project except for the covered gatewell slots (mentioned above) that no longer have temperature probes installed.  Temperature information will be distributed in a separate weekly report.

On July 24, spill for juvenile fish passage returned to 50 percent of total flow. On the same day, the hoists for bays 19 through 21 all had difficulty reopening following towboat and fish barge passage.  Bays 19 and 21 were reopened fairly quickly but the hoist for bay 20 (spillway weir bay) required repairs which were not completed until 1445 hours. 
Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	177.7
	119.8
	87.4
	64.3
	72.2
	69.4
	6.0
	     6.0


*From control room data.

Other

Invasive Species:  On July 13, the zebra mussel stations were examined and no mussels were found.  The next inspection is scheduled for approximately August 13.  

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week. 
Predatory bird counts continue with the tailwater and forebay areas being checked twice and once a day, respectively.  The tailwater area had high counts of 14 pelicans, 25 terns and 11 cormorants with an occasional gull, night heron and merganser also being observed.  No birds were seen at the bypass outfalls.  Although the water cannon continued to operate well, one to four pelicans were noted at the separator adult return outfall.  Forebay bird counts peaked at 6 grebes and 10 juvenile gulls.  No grebes were noticed in the gatewells or the juvenile fish collection gallery this week.  

Juvenile and adult lamprey research studies are in progress.                                 

Project:  Ice Harbor

Biologist:  Mark Plummer 

Technician: Stephen Jeffers
Dates:  July 24 - 30, 2009

Turbine Operation

Turbine units (1 and 3 - 6) were available for operation throughout this reporting period.  Turbine unit 2 returned to service from annual maintenance on July 30. 

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways on July 27, 28, and 29. 
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The south picketed leads are requiring frequent cleaning due to plugging with aquatic vegetation.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.7 feet, on sill with a depth of 8.3 feet, and on sill with a depth of 8.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.1 feet, on sill with a depth of 8.2 feet, and on sill with a depth of 8.1 feet.  The north shore entrance (NSE) was on sill with a depth of 9.0 feet, on sill with a depth of 6.7 feet, and on sill with a depth of 8.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  On the July 27 inspection, the north shore channel/tailwater differential was 2.1 feet.  On the July 29 inspection, the north channel/tailwater differential was 4.0 feet. This reading was of short duration while repairs were made to the entrance weir.  All other channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.  On July 26 the brakes on the NFE 2 failed.  The weir was closed in manual mode and the sister weir NFE 1 was placed into operation.  Maintenance personnel repaired the problem July 27, restored NFE 2 back to automatic operation and placed NFE 1back into standby status.  On July 28 the sonar (water elevation) detector failed in the north shore channel.  Currently, the channel elevation is being detected by the old metra-tape system.  Replacement parts for the sonar are on order.  
Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 is on standby.  Six of the available 8 south fish pumps were operated without problem.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.
STSs/VBSs:  STSs are in continuous run mode operation.  STS inspections are scheduled for August 3.  

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.
Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.    
Removable Spillway Weir:  The RSW is in the operating position.

Fish Sampling:  Juvenile fish sampling was stopped for the 2009 season after the July 17 sample due to river water temperatures approaching 70 degree F.

River Conditions

River conditions during the week are outlined in Table 1.  
Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	40.6
	33.8
	30.4
	24.0
	70
	69
	7.1
	6.0


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer gages are read 3 times a reporting period during each adult fishway inspection by fish facility personnel.  Strainer inspections are performed during STS inspections.

Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this reporting period.

Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Ken Fone 

Dates:  July 24 - 30, 2009

Turbine Operation

All turbine units were operated within the 1% operation criteria.  Turbine unit 6 was taken out of service for annual maintenance on July 13 at 0700 hours and remained out of service through this time period.  Transformer Doble testing and associated turbine unit outages began on July 20 at 0700 and continued through July 24 at 1222 hours.  The assistant project biologist discovered a turbine unit priority error this week.  Turbine unit 4 was operated from 1112 to 1320 hours on July 26 when turbine unit 5 should have been in service.  The operator quickly made the switch to turbine unit 5.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or state biologists on July 25, 26, 29 and 30.   
Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.    North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  When on sill average depth was 5.2 feet. South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.     

SSE 1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  When on sill depth was 5.6 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

Auxiliary Water Supply System:  AWS pump 3 has been out of service to replace the bearing housing and repair the diffuser assembly.  Pumps 1 and 2 were in service throughout this period.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.     

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 0.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0 to 35% surface coverage.  Gatewell slots were dipped on July 16.  No oil was observed in gatewells.

STSs/VBSs:  STS operation was changed to cycle mode on July 30 as average fork length of sockeye and chinook juveniles exceeded the 120 mm criteria.   STS/VBS inspection of intake gatewell slot 6 C was inspected on July 26.   Inspection revealed no problems.  STS/VBS inspection for the month of July is now complete with no repairs required.

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass operated with 19 orifices open.  Channel, dewatering structure and flume functioned normally.
Collection Facility:  Fish are being collected for transport.  Equipment is functioning normally. 

Transport Summary:  Every other day barging is occurring.  

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	40.9
	32.1
	17.5
	16.8
	71
	69
	5+
	3.8


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers: The main turbine unit cooling water strainers were cleaned on July13.  Fifteen juvenile lamprey mortalities were recorded.  No other fish were present.  We plan to collect this information monthly through the year unless degradation of fish due to water temperature makes this task impossible.  

Invasive Species: There were no zebra mussels observed at the monitoring stations on August 1.  The September inspection is expected to occur during the week of September 1.

Summer spill began on June 21.

Contractor illness forced the interruption of visual adult fish counts from 1315 to 1340 hours on July 27.  The scheduled fish counter arrived at work as usual, but was too sick to complete her shift.  She was sent home and another fish counter was called in to finish the shift.  

Project:  Little Goose

Biologist: Richard Weis
Dates:  July 24 - 30, 2009

Turbine Operation

Turbine units 1, 2 and 4 through 6 were available for service during this report period.  Turbine unit 3 was placed out of service on July 28 for scheduled annual maintenance.  All turbine units were operated within 1% efficiency criteria.  

Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on July 26 and 28.

Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 0.86 and 1.58 ft. (criteria 1.0 to 2.0 ft.). 

SSE1 and 2 weir depths ranged between 8.28 and 8.32 feet (criteria ≥8.0 ft), NPE1 and NPE2 weirs rested on sill and depths ranged between 5.43 and 5.62 feet (criteria ≥7.0 ft. or on sill).  NSE2 weir depths ranged between 6.14 and 6.36 feet. (criteria ≥ 6.0 ft.).  
Collection channel water velocities (criteria 1.5 to 4.0 fps) measured 2.6 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.6 and 1.8 fps.
The fall-out fence was inspected this week.  No further deterioration was observed.

Auxiliary Water Supply System:   All three fish pumps operated within criteria.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Floating forebay debris remained minimal with an estimate of 50 square feet lingering inside the trash shear boom.  

ESBSs/VBSs: All ESBSs operated satisfactorily during this report period.  Drawdown measurements were conducted on July 29 and all criteria were met.  Video inspections of ESBS/VBS were conducted June 23 – 25.  The next scheduled video inspections are scheduled for August 4 – 6.  Trash rack cleaning previously scheduled for June 16 – 17 was postponed as the crane limit switches need repair.      

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel was operated with 21 to 24 open orifices.  There were no orifice blockages during this report period.  The primary dewatering weir motor failed on July 20 and is undergoing repairs.  Flows into the bypass system are regulated with the number of open orifices (22 open).

Transportation Facility:  Collection and transport continued throughout this report period.  Daily collection numbers ranged between 301 and 1,269 for a total of 4,395.  Descaling rates the same period ranged between 0.0% and 0.9% for a mean of 0.34%.  Daily smolt mortalities ranged between 8 and 29 for a totaled of 117 (mean of 2.7% for the week).  The majority of mortalities appear to have symptoms consistent with columnaris disease.   
Transport Summary:   Every-other day barging operations continued.  All barge loading and transport operations were performed satisfactorily.
Spillway Weir:  No problems to report.  High crest operations began July 8.
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	   40.6
	35.7
	12.3
	10.1
	75.3
	69.9
	5.5
	4.5


*Ladder temperature.
Other
Inline Cooling Water Strainers: Turbine unit 4 cooling water strainers were inspected on July 8.  No fish or fish remains were observed.  No other cooling water strainers were checked this week. Continued inspections of strainers will coincide with annual turbine maintenance.  

Invasive Species:  The Zebra Mussel substrate was inspected on July 5.  No mussels were observed.   The next inspection is scheduled for August 5.

An occasional gull was observed during the report period.   

Project:  Lower Granite

Biologists: Mike Halter and Casey Watson
Dates:  July 24 - 30, 2009

Turbine Operation

Lower Granite had turbine units 1, 2, 3, 5, and 6 available for power generation at the beginning of the report week.  Turbine unit 1 was taken out of service from 0634 hours to 1609 hours on July 28 to replace the oil in a thrust bearing.  The oil temperature had been running high and the oil was foaming.  An oil sample was sent off to a lab for analysis.  Turbine unit 4 remained out of service for annual maintenance and is projected to return back to available status on July 31.  All operating turbine units were run within the established guidelines during the report period.  
Adult Fish Passage Facility
On July 24, 25, 27, and 30 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  

Fish Ladder:  All criteria were met during the week.  Since the adult trap has been out of service, the ladder weir depth at diffuser 14 has returned to within criteria.  
Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances also remained within criteria whenever the tailwater depths were sufficient to keep the gates off their seals.  (At tailwater elevations below 633.0 feet the south shore gates bottom out).  Weir depths at the south shore entrances ranged between 7.9 and 8.2 feet during the weekly inspections (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse fishway entrances were below the desired 8.0 foot criteria level on all inspections this week due to low tailwater elevations which caused the gates to bottom out and rest on their sills.  North powerhouse entrance weir depths ranged from 5.1 to 5.5 feet.  Weir depth readings at the north shore fishway entrances were out of criteria all week and ranged between 4.8 and 5.2 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.81 to 1.01 feet per second and averaged 0.95 feet per second.

Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.  The bearing work on fish pump 2 has been completed.  Fish pump 2 testing will be conducted in the near future.

Juvenile Fish Passage Facility

The facility sample rate was increased from 20.0% to 50.0% at 0700 hours on July 24.   The sample system was set to over-ride the sample and divert PIT tagged fish into the PIT-tag headbox at 0700 hours on July 28.

Forebay Debris/Gatewell Debris/Oil:   Debris levels remained very low during the week.  There were no plugging issues of any kind.  
ESBSs/VBSs:  The last video camera inspections of the ESBSs and VBSs were completed on June 19.  The next video inspections are scheduled for August.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Debris levels were very low during the report week.  As a fail-safe measure, collection gallery orifices were  back-flushed every three hours throughout the week.

Transportation Facility:  Every other day fish barging operations continued during the week at Lower Granite, Little Goose, and Lower Monumental dams.  Daily fish barge operations are taking place at McNary Dam.  A second barging operation is now taking place at McNary Dam to barge fish on the days the Lower Granite barge is not available.
Transport Summary:   Fish were barged on the odd days of the month.   Fish are also being picked up for transport at Little Goose, Lower Monumental, and McNary dams.
Removable Spillway Weir:   Nothing to report on the RSW.  

River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	41.3
	36.6
	18.7
	18.5
	69.5
	66.7
	5.0
	5.0


*Scrollcase temperature.
Other
Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on July 20.

Inline Cooling Water Strainers:   Inline cooling water strainers on turbine unit 4 were last checked for lamprey on July 14.  One lamprey (alive) was found in one strainer basket.  The other basket had evidence of 3 dead lampreys.  
Adult fish trap operations were discontinued on July 19 due to problems with the air valve control for the slide gate to the anesthetic tank and high water temperatures.  Trap operations have been suspended until the valve can be replaced and water temperatures drop to a safe level for fish handling.

As part of a multi-agency task, USGS personnel collected subyearling Chinook in the sort by code system at Lower Granite to gather length and weight information on surrogate, production, and natural groups of subyearling Chinook to characterize similarities and differences among the groups. This work will help determine a hydro system strategy to meet recovery needs for this ESU.

