U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#23-2009
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  July 31 – August 6, 2009

Turbine Operation

McNary had 11 turbine units available for power generation this week.  Turbine units 7 and 8 remain out of service for replacement of transformer T4.  This work should be completed in approximately one week.  Turbine unit 2 remains out of service for nine year overhaul.  North powerhouse priority loading remains in effect to moderate juvenile collection channel and gatewell temperatures.  All available turbine units operated within the hard constraint one percent criterion this week.  
Adult Fish Passage Facilities

On August 1, 3 and 5, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts, daily temperature monitoring and lamprey research continues.
Fish Ladders:  During measured inspections, both ladders met all Fish Passage Plan criteria except for the Washington head over weir differential (1.4’ on August 1), the Washington count station differential (measured 0.8 feet on August 1), and the Oregon count station differential (respectively measured 0.8’ and 0.6’ on August 1 and 5).  The Oregon count station picketed leads required repeated cleanings this week due to excessive milfoil accumulations.  A 55 gallon drum was also removed from the Oregon count station.  Fish passage was not impaired by the drum.  
The south Oregon exit traveling screen remains in automatic operation, with cycling frequency increased to ten times per day, 15 minutes duration per cycle.  The north Oregon exit traveling screen remains out of service.  South screen operational problems encountered this week included a triggered alarm on April 3, and continuous screen operation.  Normal operation resumed after the alarm was reset, and the continuous operation issue was resolved by resetting the lower screen differential limit setting from 0.15’ to 0.35’.  
Excess debris at the Oregon ladder exit caused trash rack differentials to increase to 1.2’ at the beginning of the week, then to 2.9’ by August 3.  On August 3 and 4, project personnel attempted to remove debris from the vicinity.  On August 4, the top trash rack for the auxiliary water supply was also cleaned, reducing the trash rack differential to 1.0’.  A dive has been scheduled for August 17 and 18 to repair the north traveling screen and clean the remaining trash racks. Until then, more intensive debris and differential monitoring efforts will continue.  

Fishway Entrances and Collection Channel:  All Washington ladder inspection points met criteria except on August 1 when W3 measured 7.9 feet.  All Oregon ladder inspection points met criteria except for the north powerhouse pool differential on August 1 and 3 (0.8 and 0.6 feet, respectively), NFEW2 on August 1 and 5 (8.9 feet both days), NFEW3 on August 1 (measured 8.9 feet), and SFEW1 on August 1 and 3 (both measured 8.9 feet).  The LED (electronic display) for NFEW3 became functional after replacement on July 31.  The collection channel velocity averaged 1.5 feet per second this week.    

Auxiliary Water Supply System:  Although repairs have been completed, fish pump 3 remains out of service.  Maintenance personnel will attempt to place fish pump #3 into operation on approximately August 12.  Pumps 1 and 2 operated all week with blade angles of 30 degrees.  As mentioned above, the auxiliary water supply trash racks were cleaned on August 3 and 4.  Cleaning activities on August 4 required the closure of the 1,000 CFS supply line from 1302 to 1551 hours.  The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool and the Wasco County PUD unit had no interruptions in service this week.

Juvenile Fish Passage Facility

Fish collection for daily barge transport continued.  Barges loaded on odd numbered days in August began their trips at Lower Granite Dam.  Barges loaded on July 31 and even numbered days in August began their trips at McNary Dam.  For the report week, 44,290 smolts were collected for transport.  Daily facility mortality rates ranged from 0.6 to 1.7 percent this week.  Juvenile shad are now present with 21,673 being collected for the week. 

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains very light though some woody debris and Eurasian milfoil remain near the Oregon ladder exit as described above.  Turbine unit trash rack differentials remained low and none of these trash racks were cleaned this week. Slight oil sheens were removed from three gatewell slots.  Gatewell slots 7B, 7C, 8A and 8B remain covered to prevent contamination should a spill take place during the course of T4 transformer replacement.
ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  Screens in slots 11C and 13A remain in transducer bypass mode.  The screen in slot 9C triggered an alarm once this week and resumed normal operation after the alarm was reset.   ESBS video camera inspections were conducted in turbine unit 1 this week and no problems were observed.  This inspection included the screen in slot 1B which was missed during the last video inspection of turbine unit 1.  VBS monitoring revealed no screens out of criteria.  However, 3 VBSs were cleaned as a preventive measure.    

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, there were 42 orifices opened.  On August 2, the orifice at slot 9A was found closed approximately 1.5 hours after orifices were cycled.  No unusual fish injuries or mortalities were noted and proper orifice cycling was reviewed with the technician involved.  On August 3, a stick was removed from the rectangular screen cleaning mechanism.  No other problems were encountered and all automated systems operated well.  The channel was monitored during VBS cleaning operations.
Transportation Facility:  Fish collection for barge transport continued.  The primary (A and B) PIT tag diversion gates are in service and the secondary (C and D) PIT/bypass gates remain closed.  Sample gates operated satisfactorily this week.  Sample gates are normally overridden by PIT tag gate operation whenever the sample rate is 20% or greater.  PIT tag gates do not operate during sample gate openings if the sample rate is less than 20%.  Maintenance this week included water balloon tests of the return to the river lines (no ruptured balloons means no obstructions or debris), moveable flume maintenance, and the servicing of 2 raceway release valves.  
Transport Summary:  Barge departures took place daily from July 31 to August 6.  All barges were loaded without incident.  On August 6, a semi-truck and 3,500 gallon tanker were sent to Bonneville Dam for a test release at the recently modified truck pad.  No significant problems were found.              

River Conditions

River conditions during the week are outlined in Table 1 with data provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Water clarity data continues to be provided by the control room.  The smolt monitoring staff continued gathering water temperature data throughout the project except for the covered gatewell slots (mentioned above) that no longer have temperature probes installed.  On August 5, a weather cooling trend began which should improve river conditions.  Temperature information will be distributed in a separate weekly report.  

Since July 24, spill for juvenile fish passage has been 50 percent of total flow.  The spillway continues to be opened and closed for towboat and fish barge arrivals and departures from the fish facility.  On August 2, the hoist for bays 6 and 16 would not close the final foot.  The towboat and barge were able to tie up at the facility under this condition.  The problem was resolved prior to departure.  On August 4, a GDAC (software) problem delayed the reopening of the spillway.  In addition, the hoist at bay 19 (where TSW1 is located) became stranded at a 6 foot opening until the hoist was reset.  
Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	159.3
	110.7
	78.9
	53.9
	73.1
	72.2
	6.0
	     6.0


*From control room data.

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week. 
Invasive Species:  On July 13, the zebra mussel stations were examined and no mussels were found.  The next inspection is scheduled for approximately August 13.  

Predatory bird counts continued with the tailwater and forebay areas being checked twice and once a day, respectively.  The tailwater area had high counts of 2 pelicans, 31 terns and 10 cormorants.  No birds were seen at the bypass outfalls.  Although the water cannon continued to operate well, an occasional pelicans was noted at the separator adult return outfall.  Forebay bird counts peaked at 4 grebes and 2 gulls.  One cormorant was observed at the Oregon ladder count station.  No grebes were noticed in the gatewells or in the juvenile fish collection gallery this week.  

Juvenile and adult lamprey research studies are in progress.                                 

Project:  Ice Harbor

Biologist:  Mark Plummer 

Technician: Stephen Jeffers
Dates:  July 31 – August 6, 2009

Turbine Operation

Turbine units 1 – 4 were available for operation this entire reporting period.  Turbine units 5 and 6 went out of service August 3 for annual maintenance. 

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways on August 3, 4, and 6. 
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The south picketed leads are requiring frequent cleaning due to plugging with aquatic vegetation.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 7.5 feet, on sill with a depth of 7.7 feet, and on sill with a depth of 7.7 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.4 feet, on sill with a depth of 7.7 feet, and on sill with a depth of 7.7 feet.  The north shore entrance (NSE) was off sill with a depth of 5.5 feet, off sill with a depth of 5.6 feet, and off sill with a depth of 5.4 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The north shore channel/tailwater differentials were 2.4, 2.3, and 2.5 feet. The shift operator adjusted the setting on the channel/tailwater differential.  All other channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.  On July 28, the sonar elevation detector failed at the north shore channel inspection location.  Currently, the north shore channel elevation is being measured by the old metra-tape system.  Replacement parts for the sonar equipment are on order.  
Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 is on standby.  Six of the available 8 south fish pumps were operated without problems.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.
STSs/VBSs:  STSs were switched to cycle mode operation on August 3 due to the size of sub-yearling Chinook being greater than 120 mm at Lower Monumental Fish Facility.  STS inspections were performed on turbine units 5 and 6 August 3.  No problems were found.  STS inspections for units 1 and 2 are scheduled for August 18.  STS inspections for turbine units 3 and 4 are scheduled for August 25.  

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.  The power supply wire system to the screen cleaner in the collection channel malfunctioned August 4.  Parts needed for repairs have been ordered and shipped.  The juvenile collection channel water elevations and the incline screen area are being monitored by power house operators and fish facility personnel.  
Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.    
Removable Spillway Weir:  The RSW is in the operating position.

River Conditions

River conditions during the week are outlined in Table 1.  
Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	39.6
	30.2
	29.1
	20.1
	70
	69
	8.6
	7.0


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer gages are read 3 times a reporting period during each adult fishway inspection by fish facility personnel.  Visual strainer inspections were performed on turbin units 5 and 6 during the August 3 STS inspections.  Two lampreys were found in the turbine unit 5 strainers and 1 lamprey was found in the turbine unit 6 strainers.  All 3 lampreys were found dead.  

Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this week.

Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Ken Fone 

Dates:  July 31 – August 6, 2009

 Turbine Operation

All turbine units were operated within the 1% operation criteria.  Turbine unit 6 was taken out of service for annual maintenance on July 13 at 0700 hours and remained out of service through this time period.  Turbine unit 1 was taken out of service on August 3 from 0705 hours to 1630 hours for STS inspections and to repair the STS in gatewell slot 1C.  Turbine units 2 through 5 were taken out of service one at a time on August 4 for STS inspections.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or state biologists on August 1, 2, 4, and 5.   
Fish Ladders:  Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel:  NPE1 and NPE2 weir gates were within depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was within criteria (1’-2’) on all inspections.  

SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections, with an average depth of 5.2 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.     

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections, with an average depth of 5.7 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

Auxiliary Water Supply System:  AWS pump 3 has been out of service to replace the bearing housing and repair the diffuser assembly.  Pumps 1 and 2 were in service throughout this period.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.  The average rpm of pumps 1 and 2 was increased from 71 to 74 on August 4 to increase the north collection channel velocity, which was 1.1 feet per second (criteria: 1.5-4.0 fps) on August 1.        

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 1 square yard of forebay debris observed during this period.  Gatewell debris ranged from 0% to 25% surface coverage.  No oil was observed in the gatewells.

STSs/VBSs:    STS operation was changed to cycle mode on July 30 as the average fork lengths of sockeye and chinook juveniles exceeded the 120mm criteria.  Turbine unit 1-5 STSs were inspected on August 3 and 4, with no substantial problems observed.  Turbine unit 6 STSs did not need to be inspected, because the turbine unit has been out of service since last month’s inspections.  On August 3, the STS in gatewell slot 1C was raised up on deck as part of the intake crane tugger test and to make some minor STS repairs.  This included STS mesh repairs and the replacement missing fasteners that hold the mesh to the frame.  Closer examination revealed that about seven of the cross-bars on the frame were loose at one end due to missing or loose bolts.  None of these problems presented any harm to fish.  Repairs were completed the same day. 

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass operated with 19 orifices open.  Orifice 3A13 light was found burned out on August 2 and was replaced the next day.  Orifice 6C36 light was found burned out on August 3.  This new brand of lighting at 6C36 has burned out frequently and will require further investigation to solve the problem.  The other orifice in the gatewell has also been open, with a working light.  Orifice 5B27 became stuck closed on August 4, so the other orifice in the gatewell was opened the same day.  The channel, dewatering structure and flume functioned normally.
Collection Facility:  Fish are being collected for transport.  Equipment is functioning normally. 

Transport Summary:  Every other day barging is occurring.  

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	37.9
	29.3
	17.5
	16.9
	71
	70
	5+
	4.6


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers: The main unit cooling water strainers were cleaned on July 13.  Fifteen juvenile lamprey mortalities were recorded.  No other fish were present.  We plan to collect this information monthly through the year unless degradation of fish due to water temperature makes this task impossible.  
Invasive Species: There were no zebra mussels observed at the monitoring stations on August 1.  September inspection is expected to occur during the week of September 1.

Summer spill began on June 21.

The turbine unit 6 scrollcase was dewatered on July 28 (during the last report period) for annual maintenance.  One channel catfish was salvaged and released into the river.  No other fish were observed.

Project:  Little Goose

Biologist: George Melanson
Dates:  July 31 – August 6, 2009

 Turbine Operation

Turbine units 1, 2 and 4 through 6 were available for service during this report period.  Turbine unit 3 remained out of service for scheduled annual maintenance.  All turbine units were operated within 1% efficiency criteria.  

Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on July 31, August 1 and 4.

Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.14 and 1.54 ft. (criteria 1.0 to 2.0 ft.). 

SSE1 and 2 weir depths ranged between 8.14 and 8.18 feet (criteria ≥8.0 ft), NPE1 and 2 weirs rested on sill and depths ranged between 5.16 and 5.54 feet (criteria ≥7.0 ft. or on sill).  NSE1 weir depths ranged between 6.18 and 6.26 feet (criteria ≥ 6.0 ft.).  On August 1, NSE 2 measured below criteria at 5.76 feet.  NSE2 was measured within criteria on July 31 and August 4 recording depths of 6.12 and 6.06 feet respectively (criteria ≥ 6.0 ft.).  
Collection channel water velocities (criteria 1.5 to 4.0 fps) ranged between 2.3 and 2.7 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.8 and 2.0 fps.
The fall-out fence was inspected this week.  No further deterioration was observed.

NPE3 (a concrete lift gate) which is normally closed, has deteriorated from water forces caused by spill over spillway 1.  Spill over spillway 1 forces collection channel water to remain within the channel and to meet channel to tailwater head differentials criteria at fishway entrances.  Repairs to NPE 3 are scheduled towards the end of the fish passage season.   

Auxiliary Water Supply System:   All three fish pumps operated within criteria.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Several pieces of floating forebay debris were observed inside the trash/shear boom.  Gatewells remained clear of debris and contaminants.  

ESBSs/VBSs: All ESBSs operated within criteria this report period.  Video inspections of ESBS/VBS were conducted August 4 – 5.  All screens were in proper operating condition.  The next scheduled video inspections are scheduled for October 6 - 8.  Trash rack cleaning scheduled for June 16 – 17 was postponed awaiting repairs to the limit switches on the crane.      

Orifices, Collection Channel, Dewatering Structure, and Flume:  The collection channel was operated with 21 to 22 open orifices.  There were no orifice blockages during this report period.

The primary dewatering weir motor failed on July 20.  The motor is undergoing repairs.  Flows into the bypass system are regulated with the number of open orifices.

Transportation Facility:  Collection and transport continued this report period.  Daily collection ranged between 471 and 1,247 for a total of 4,848 for the week.  Descaling rates this report period ranged between 0.0% and 1.1% for a mean of 0.14%.  Daily smolt mortalities ranged between 8 and 26 for a totaled of 105 (mean of 2.17%).  The majority of mortalities appear to be disease (presumed columnaris) related.   

On August 6 the facility switched to primary bypass from 0730 to 0900 hours to clean the separator.  Approximately 3 cubic yards of woody debris and mud was removed.  In addition an estimated 1,000 juvenile lamprey (mostly pre-adult stage) were salvaged and returned to the river.
Transport Summary:   Every-other-day barging operations continued.  All barge loading and transport operations were performed satisfactorily.
Spillway Weir:  No problems to report.  High crest operations began July 8.
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	   39.5
	30.9
	11.8
	9.2
	74.6
	69.7
	5.0
	4.2


*Ladder temperature.
Other
Inline Cooling Water Strainers: Turbine unit 4 cooling water strainers were inspected on July 8.  No fish or fish remains were observed.  No other cooling water strainers have been inspected since then.  Continued inspections of strainers will coincide with annual turbine maintenance.  

Invasive Species:  The Zebra Mussel substrate was inspected on August 6.  No mussels were observed.   The next inspection is scheduled for September 2.

Up to six gulls were observed in the forebay during the report period.   

Project:  Lower Granite

Biologists: Mike Halter and Casey Watson
Dates:  July 31 – August 6, 2009

Turbine Operation

Lower Granite had turbine units 1, 2, 3, 5, and 6 available for power generation at the beginning of the report week.  Turbine unit 4 was returned to service following annual maintenance at 1021 hours on August 3.  Turbine unit 6 was taken out of service for annual maintenance at 1116 hours on August 3 and remained out of service for the remainder of the report week.  All operating turbine units were run within the established guidelines during this report period.  
Adult Fish Passage Facility
On July 31 and August 1-3 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  

Fish Ladder:  All criteria were met during the week.  Since the adult trap has been out of service, the ladder weir depth at diffuser 14 has been within criteria.  
Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances also remained within criteria whenever the tailwater depths were sufficient to keep the gates off their seals.  (At tailwater elevations below 633.0 feet the south shore gates bottom out).  Weir depths at the south shore entrances ranged between 7.9 and 8.2 feet during the weekly inspections (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse fishway entrances were below the desired 8.0 foot criteria level on all inspections this week due to low tailwater elevations which caused the gates to bottom out and rest on their sills.  North powerhouse entrance weir depths ranged from 5.1 to 5.5 feet.  Weir depth readings at the north shore fishway entrances were out of criteria all week and ranged between 4.8 and 5.2 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.81 to 1.01 feet per second and averaged 0.95 feet per second.

Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.  The bearing work on fish pump 2 has been completed.  Fish pump 2 testing will be conducted in the near future.

Juvenile Fish Passage Facility

The facility sample rate remained at 50% during the week.

Forebay Debris/Gatewell Debris/Oil:   Debris levels remained very low during the week.  There were no plugging issues of any kind.  
ESBSs/VBSs:  The last video camera inspections of the ESBSs and VBSs were completed on June 19.  The next video inspections are scheduled in August.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   As a fail-safe measure, collection gallery orifices were back-flushed every three hours throughout the week.

Transportation Facility:  Every other day fish barging operations continued during the week at Lower Granite, Little Goose, and Lower Monumental dams.  Barge departing from Lower Granite Dam also pick up fish every other day at McNary Dam.  A second barge operation is taking place at McNary Dam to pick up fish on the days when a Lower Granite barge is not available.
Transport Summary:   All operations continue to go smoothly.  Fish barges are departing Lower Granite Dam on the even numbered days during the month of August.  The last fish barge is scheduled to depart Lower Granite on August 14.  Fish trucking operations are scheduled to begin on August 16.
Removable Spillway Weir:   Nothing to report on the RSW.  

River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	40.6
	32.6
	18.8
	18.6
	69.5
	66.2
	5.0
	5.0


*Scrollcase temperature.
Other
Inline Cooling Water Strainers:   Inline cooling water strainers on turbine unit 4 were last checked for lamprey on July 14.  One lamprey (alive) was found in one strainer basket.  The other basket had evidence of 3 dead lamprey.  
Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on July 20.

Adult fish trap operations were discontinued on July 19 due to problems with the air valve control for the slide gate to the anesthetic tank and also high water temperatures.  Trap operations are tentatively scheduled to resume on August 18 if water temperatures are low enough to begin work.  The goal at the adult trap this year is to maintain a 12% sample rate through the fall season.  In addition, a goal of 2,000 unclipped (wild) steelhead are to be PIT-tagged for Idaho Fish and Game.

