U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#26-2009
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  August 21 - 27, 2009

Turbine Operation

McNary had seven to eight turbine units available for power generation this week.  Turbine units 7 and 8 remain out of service for replacement of transformer, T4, which should be completed in early September.  Turbine units 1 and 2 respectively remain out of service for annual maintenance and 9 year overhaul.  Both are expected to return to service in mid-September.  Turbine unit 5 also remains out of service for annual maintenance and is expected to return to service on August 31 when a portable crane will be available to move the headgates.  Other turbine units outages this week took place from August 22 to 23 (turbine unit 9, failed ESBS in the C slot) and on August 25 (turbine units 10 and 13, ESBS camera inspections, 42 minutes total outage time).

Turbine unit 6 remains out of service as the failed intake deck crane (reported last week) is still attached to the headgate in slot 6B.  Project personnel plan to disconnect the headgate and move the disabled crane to the north end of the powerhouse in the near future.  A mobile crane can then be used to lift the head gate and return turbine unit 6 to service.  Although intake deck crane repair parts have been ordered and repairs have been scheduled, the crane will also require inspection and testing by a certified crane inspector following completion of repairs.  
North powerhouse priority loading remains in effect to moderate juvenile collection channel and gatewell temperatures.  All available turbine units operated within the hard constraint one percent criterion throughout this report period.

Adult Fish Passage Facilities

On August 22, 24 and 27, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts, daily temperature monitoring and lamprey research continued.      
Fish Ladders:  Both ladders met all Fish Passage Plan criteria during inspections.  As previously reported, the north Oregon ladder exit traveling screen repairs will require an extended outage to complete.  This work will likely take place during the winter maintenance season.  The south traveling screen is operating well and continues to supply sufficient water to meet facility needs.  On August 21, the south screen underwent routine maintenance without incident.  The trash rack and screen differentials remained low and unchanged from previous readings.  Debris and differential monitoring continues.       

Fishway Entrances and Collection Channel:  Most Washington ladder inspection points met criteria this week.  Locations not meeting criteria included the pool differential on August 24 (measured 2.1 feet), W2 on August 22 and 24 (measured 7.8 feet on both dates) and W3 on August 24 (measured 7.6 feet).  Weir readings are being affected by low tailrace elevations which cause the entrance gates to bottom out on the sill limit switch.  
All Oregon ladder inspection points met criteria except for the north powerhouse pool differential which measured 0.7 to 0.9 feet all through the week and SFEW1 which measured 8.9 feet on August 22.  On August 27, NFEW2 and NFEW3 were recalibrated.    The collection channel velocity average 1.6 feet per second this week.    
Auxiliary Water Supply System:   All three fish pumps were in operation this week with blade angles of 26 to 30 degrees except as described here.  Fish pumps 1 and 3 tripped breakers on August 21, 25, and 26 due to low cooling water flows with outages respectively lasting 24 and 11 minutes on August 21 and 24.  On August 26, fish pump 1 was out of service for 3.5 hours and fish pump 3 was out of service for 20.3 hours – also due to low cooling water flows.  Fish pump 3 triggered an alarm on August 24 then was removed from service for 2.2 hours while being examined by a troubleshooter.  As mentioned last week, the potable water system which is used for many project functions including fish pump cooling water, is experiencing problems with the well pump, supply lines, and the storage reservoir liner.    On August 29, a dive is scheduled for the removal of the damaged liner which should improve the potable water flow problem.  Despite the intermittent pump outages, fish passage remains strong.  The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool and the Wasco County PUD unit had no interruptions in service this week.

Juvenile Fish Passage Facility

Daily collection for every other day truck transport continues.  For the report week, 14,350 smolts and 5,315 juvenile shad were collected.  Facility mortality rates averaged 1.0 percent for the same period.     

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains very light and no problems were encountered.  Trash rack differentials remained low and no racks were cleaned this week.  Gatewell slots 7B, 7C, 8A and 8B remain covered to prevent contamination should a spill take place during the course of T4 transformer replacement.  
ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  The screen in slot 11C remains in transducer bypass mode. The screen in slot 9C triggered alarms repeatedly on August 22 and 23 before being taken out of service.  The screen was returned to service August 24 after being placed in transducer bypass mode.  ESBS video camera inspections were conducted in turbine units 10 and 13 this week and all inspected screens were found in satisfactory condition.  VBS monitoring revealed no screens out of criteria and no screens were cleaned during this report period.
Because of increased river flows and increased power demand on August 26, the operator on duty brought another turbine unit on line to avoid increased VBS differentials.  Spreading the powerhouse electrical load with an additional turbine unit in service meant individual generators are operated at lower power levels and decreased the risk of VBSs exceeding their maximum allowed differentials.  Such precautions are prudent as the disabled forebay intake deck crane is normally is used to perform ESBS maintenance, VBS maintenance and trash rack cleaning.  Such maintenance work will not be possible until mobile crane service becomes available.                                              

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, there were 42 opened orifices.  No problems occurred and all channel systems operated well in automatic mode.                

Transportation Facility:  Fish collection for transport continued.  The primary (A and B) PIT tag diversion gates are in service and the secondary (C and D) PIT/bypass gates remain closed and off.  Sample gates operated satisfactorily this week.  Regularly scheduled maintenance continued as did water balloon tests.  Water balloon tests determine whether there are any blockages in the river return lines.  A ruptured balloon indicates an obstruction.  

Transport Summary:  Truck trips took place on August 22, 24 and 26 without incident.  On August 26, the driver modified the cistern grating at the release site so that a hose nozzle could be inserted whenever water supply pipes are flushed.     

                                                         River Conditions

River conditions during the week are outlined in Table 1 with data provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Water clarity data continues to be provided by the control room.  The smolt monitoring staff continues gathering water temperature data throughout the project except for the covered gatewell slots (mentioned above) that no longer have temperature probes installed. This information will be distributed in a separate weekly report.   Temperature monitoring efforts will cease September 1.  Spill for juvenile fish passage continued at 50 percent of total flow as did spill pattern changes in support of towboat and barge entering and exiting the locks.  The summer spill program will conclude September 1 at 0001 hours. 
Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	138.8
	110.1
	69.3
	55.2
	70.6
	69.5
	6.0
	     6.0


*From control room data.

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week. 
Invasive Species:  On August 10, the zebra mussel stations were examined and no mussels were found.  The next inspection is scheduled for approximately September 10.

Predatory bird counts continued with the tailwater and forebay areas being checked twice and once a day, respectively.  The tailwater area had high counts of 42 terns, 200 gulls and 13 cormorants.  No birds were seen at the bypass outfalls.  The water cannon continued to operate well.  Only an occasional osprey was seen in the forebay.  No grebes were noticed this week.  

GBT monitoring activities will also conclude with the cessation of spill on September 1.  
Project:  Ice Harbor

Biologist:  Mark Plummer 

Technician: Stephen Jeffers
Dates:  August 21 - 27, 2009

Turbine Operation
Turbine units 1, 2, 5, and 6 were available for operation this entire reporting period.  Turbine unit 3 went out of service August 25 for annual maintenance.  Turbine unit 4 went out of service August 12 for annual maintenance and electrical repairs (loose connection in the transformer canyon).  Turbine unit 4 also remains out of service for repairs to the small ripped hole found in the vertical barrier screen (VBS) last week.  

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways August 24, 25, and 26. 
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The south picketed leads are requiring cleaning due to plugging with aquatic vegetation.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 7.1 feet, on sill with a depth of 7.4 feet, and on sill with a depth of 7.7 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.2 feet, on sill with a depth of 7.5 feet, and on sill with a depth of 7.7 feet.  The north shore entrance (NSE) was on sill with a depth of 6.9 feet, on sill with a depth of 6.0 feet, and on sill with a depth of 6.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All other channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.  The south and center entrance gates (SFE-1 and NFE-2) are being lowered to reduce entrance velocities to benefit lamprey passage.  This operation began July 20 and occurs between the hours of 2100 hours and 0400 hours and will continue through the end of September.
Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 is on standby.  Six of the available 8 south fish pumps were operated without any problems.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.
STSs/VBSs:  STS inspections took place in turbine unit 3 on August 25.  There were no problems to report.  Turbine unit 4 remained out of service for repairs to the ripped hole found in the vertical barrier screen (VBS).  

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.  The power supply wire system to the screen cleaner in the collection channel continues to malfunction.  After repairs were made August 20, the wire system failed again the subsequent evening.  Screen cleaner repair efforts continue and parts have been ordered.  In the meantime, the screen cleaner is being operated manually once per day.  The juvenile collection channel water elevations and the incline screen area are being monitored by Power House Operators and Fish Facility Personnel.  
Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.    
Removable Spillway Weir:  The RSW is in the operating position.

River Conditions

River conditions during the week are outlined in Table 1.  
Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	36.4
	25.4
	29.6
	15.6
	70
	69
	7.0
	6.8


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer gages are read 3 times a reporting period during each adult fishway inspection by fish facility personnel.  During the turbine unit 3 STS inspection performed this period, the strainer was checked and there was nothing unusual to report.

Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this reporting period.

Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Ken Fone 

Dates:  August 21 - 27, 2009

Turbine Operation

All available turbine units operated within the 1% operation criteria.  Turbine unit 6 was taken out of service for annual maintenance on July 13 at 0700 hours and returned to service on August 24 at 1700 hours.  Turbine unit 4 was taken out of service for annual maintenance on August 25 at 0715 hours.  

Adult Fish Passage Facility

The adult fishway was inspected by Corps or state biologists on August 22, 25, 26 and 27.   
Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NPE1 and NPE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.    North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections, with an average depth of 5.2 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.     

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections, with an average depth of 5.6 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

Auxiliary Water Supply System: AWS pump 3 remains out of service to in support of bearing housing replacement and diffuser assembly repair.  Pumps 1 and 2 were in service throughout this period.  Pump 3 remains “bulkheaded off” to minimize water loss during two-pump operation.          

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0 to 16% surface coverage.  No oil was observed in the gatewells.

STSs/VBSs:    STS operation was changed to cycle mode on July 30 as the average fork length of sockeye and Chinook juveniles exceeded the 120mm criteria.  The next STS inspection is scheduled for September 5 and 6.

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass operated with 20 orifices open.   Channel, dewatering structure and flume functioned normally.
Collection Facility:  Fish are being collected for transport.  All equipment is functioning normally. 

Transport Summary:  Every-other-day midi-tanker transport began on August 16 and continued through this period. 

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	36.2
	24.3
	17.5
	12.2
	68.4
	68
	5+
	4.0


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers: The main unit cooling water strainers were cleaned on August 19.  No juvenile lamprey or other fish were present.  We plan to collect this information monthly through the year unless degradation of fish due to water temperature makes this task impossible.  

Invasive Species: There were no zebra mussels observed at the monitoring stations on August 1. The September inspection is expected to occur during the week of September 1.

Summer spill began on June 21.  Spill is scheduled to cease with the end of August.

Project:  Little Goose

Biologist: Richard Weis
Dates:  August 21 - 27, 2009

Turbine Operation

Turbine units 2, 3 and 4 were available for power generation throughout this report period.  Turbine unit 1 was removed from service on August 17 for annual maintenance.  Turbine units 5 and 6 remained out of service following Doble tests due to a faulty bushing.  All available turbine units were operated within 1% efficiency criteria.  

Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on August 23, 25 and 27.

Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.22 and 1.50 ft. (criteria 1.0 to 2.0 ft.). 

SSE1 and 2 weir depths ranged between 8.20 and 8.26 feet (criteria ≥8.0 ft), NPE1 and 2 weirs rested on sill and depths ranged between 4.90 and 5.46 feet (criteria ≥7.0 ft. or on sill).  NSE1 and 2 weir depths ranged between 5.70 and 6.22 feet (criteria ≥ 6.0 ft.).  On August 27, a trouble report was submitted to check the NSE weir calibration accuracy.    
Collection channel water velocities (criteria 1.5 to 4.0 fps) ranged between 2.6 and 3.1 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.6 and 1.84 fps.
Auxiliary Water Supply System:   All three fish pumps operated within criteria.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay and gatewells remained clear of debris and contaminants.  

ESBSs/VBSs: All ESBSs operated within criteria this report period.  All screens were in proper operating condition except for the screen in slot 3C.  This screen previously generated several trouble reports due to limit switch problems.  The switch was adjusted and the screen returned to normal operation.  The next scheduled video inspections are scheduled for October 6 - 8.  A large log appears to be lodged against unit 1’s three intakes that prevented a complete raking of the trash racks.  A plan of action is being formulated to remove the log.    

Orifices, Collection Channel, Dewatering Structure, and Flume:  The collection channel was operated with 21 to 22 open orifices.  There were no orifice blockages during this report period.

The primary dewatering weir motor failed on July 20.  Repairs are on standby - awaiting parts.  Water flow volume into the bypass system is regulated with the number of open orifices.

Transportation Facility:  Collection and transport continued throughout this report period.  Daily collection ranged between 40 and 90 for a total of 450 for the week.  Descaling was not observed this report period (i.e.: a 0.0% descaling rate for the week).  Daily smolt mortalities ranged between 0 and 4 for a totaled of 14 for the report period (3.1%).  The majority of mortalities appear to be disease (presumed columnaris) related.   

Transport Summary:  Alternate day truck transport operations using the 300-gallon midi tank started on August 16.  Salt in small concentrations of approximately 1 g/L is added to the midi-tank water to treat potential Columnaris disease and reduce stress.  All truck loading and transport operations were performed satisfactorily.  During the August 26 trip, one unclipped Chinook sub-yearling mortality was reported (presumed Columnaris related).
Spillway Weir:  TSW is in operation.
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	   38.2
	26.2
	11.6
	9.7
	68.9
	68.3
	5.0
	4.5


*Ladder temperature.
Other
Inline Cooling Water Strainers: Cooling water strainers were checked on August 27.  Turbine units 1-6 were inspected and no fish were observed.

Invasive Species:  The Zebra Mussel substrate was inspected on August 6.  No mussels were observed.   The next inspection is scheduled for September 2.

Up to 11 cormorants were observed in the forebay during this report period.   

Project:  Lower Granite

Biologists: Mike Halter and Casey Watson
Dates:  August 21 - 27, 2009

Turbine Operation

Lower Granite had turbine units 1, 2, 3, and 4 available for power generation at the beginning of the report week.  Turbine unit 5 was not available for full generation at the beginning of the week due to transformer T2 remaining off line.  Turbine unit 5 was returned to available status at 1419 hours on August 25.  Turbine unit 6 remained out of service during the report week for annual maintenance.     
Adult Fish Passage Facility
On August 22, 24, 25 and 26 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.   

Fish Ladder:  All criteria were met during the week.    
Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were within criteria whenever the tailwater depths were sufficient to keep the gates off their seals.  (At tailwater elevations below 633.0 feet the south shore gates bottom out).  Weir depths at the south shore entrances ranged between 7.5 and 8.1 feet during the weekly inspections (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse fishway entrances were below the desired 8.0 foot criteria level on all inspections this week due to low tailwater elevations which caused the gates to bottom out and rest on their sills.  (At elevations below 636.0 feet the north powerhouse gates bottom out).  North powerhouse entrance weir depths ranged from 4.5 to 5.3 feet.  Weir depth readings at the north shore fishway entrances were out of criteria all week and ranged between 5.1 and 5.4 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.86 to 1.08 feet per second and averaged 0.95 feet per second.

Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.  

Juvenile Fish Passage Facility

The facility sample rate remained at 100% during the report week.

Forebay Debris/Gatewell Debris/Oil:   Debris levels remained very low during the week.  There were no plugging issues of any kind.  
ESBSs/VBSs:  ESBS/VBS video inspections took place on August 21-23.  A number of problems were found with the VBSs during this inspection.  A bar was missing 3 bolts on the top VBS in slot 3A.  A large amount of debris was encountered 22 feet down on a VBS in slot 3B (possible tear).  Debris and a gap in the screen material were noted 29 feet down on the VBS in slot 4B.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   As a fail-safe measure, we continued to backflush collection gallery orifices every three hours throughout the week.

Transportation Facility:  The project remained at a 100% sample rate during the entire week.  Sample fish were worked up every other day in the lab and directly loaded onto the fish transport truck.
Transport Summary:   Fish trucking operations to Bonneville continued during the week.  Due to low fish numbers, and a 100% sample rate, the project used the midi-tanker for all trucking operations during the week.  All operations proceeded smoothly.
Removable Spillway Weir:   Nothing to report on the RSW.  

River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	38.8
	26.5
	18.7
	16.2
	65.7
	63.5
	5.0
	5.0


*Scrollcase temperature.
Other
Inline Cooling Water Strainers:   Inline cooling water strainers on turbine unit 4 were last checked for lamprey on July 14.  One lamprey (alive) was found in one strainer basket.  The other basket had evidence of 3 dead lamprey.  
Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on August 17.

Adult fish trap operations resumed on August 18 with fish ladder water temperatures in the high 60 degree range.  The sample rate was set at 12% and is projected to remain at that level through the duration of the fall season.  In addition, 5,000 unclipped (wild) steelhead are to be PIT-tagged for the Idaho Department of Fish and Game.

