U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#30-2009
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  September 18 -24, 2009

  Turbine Operation

McNary had nine to eleven turbine units available for power generation this week.  Turbine units 1 and 2 respectively returned to service on September 18 from annual maintenance and nine-year overhaul.  Turbine unit 2 was taken out of service for 6 hours on September 21 in support of governor work.  Doble tests also took place on September 21.  Turbine unit 5 and transmission line 3 were removed from service in support of these tests.  Turbine unit 5 should return to service early next week.  Turbine unit 6 remains out of service due to the out of position headgate in slot B, and should also return to service next week.  Turbine units 9 and 10 are expected to remain out of service in support of transformer T5 replacement for approximately a month.  For safety reasons, portable crane work near transmission line 6 required turbine units 11 and 12 taken out of service for 14.3 hours on September 23 and 24.  All available turbine units operated within the hard 1% efficiency criterion this week.    

Adult Fish Passage Facilities

On September 19, 21 and 23, McNary fishery biologists performed measured inspections of the adult fishways.  Adult fish and night time lamprey counting continues.  

Fish Ladders:  The Oregon ladder met all Fish Passage Plan criteria.  The Washington ladder met most of the criteria this week.  Washington ladder locations not meeting criteria included head over weir and count station differentials on September 19 (respectively measured 1.4 and 0.8 feet) and count station differentials on September 23 (measured 0.6 feet).  Washington count station differentials met criteria after the picketed leads were cleaned on September 19 and after the set point was adjusted on September 23.  The Washington exit triggered an alarm once this week and normal operation resumed after the alarm was reset.  The south traveling screen operated well and continues to supply sufficient water to meet facility needs.  Trash rack and traveling screen differentials remain low and unchanged.  Debris and differential monitoring continues.       

Fishway Entrances and Collection Channel:  All Washington ladder inspection points were in criteria.  On September 24, the Washington ladder entrance weirs received scheduled maintenance.  Oregon ladder inspection points not meeting criteria included the north powerhouse pool differential (measured 0.9’ on September 19 and 21) and SFEW1 (measured 8.8 feet on September 19).  All other Oregon ladder inspection points met criteria this week.  Collection channel velocities averaged 1.7 feet per second.    
Auxiliary Water Supply System:   All three fish pumps operated this week with blade angles of 22 to 30 degrees.  Three outages were recorded, two on September 18 and one on September 23.  On September 18, pumps 1 and 2 were out of service 15 minutes for an electrical bus switch.  Later the same day, all three pumps were forced out of service for 40 minutes due to low potable cooling water flow.  On September 23, all three pumps tripped breakers and went out of service for 20 minutes, also due to low cooling water flows.  The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool and the Wasco County PUD unit had no interruptions in service this week.

Juvenile Fish Passage Facility

Daily collection for every other day truck transport continues.  For the report week 980 smolts and 5,455 juvenile shad were collected.  On September 18, four power outages totaling 39 minutes duration occurred at the juvenile facility as transmission line 1 was taken out of service.  Fore safety reasons, outages were necessary when mobile crane work took place in the vicinity of turbine units 1 and 2.  Three sample gate openings were missed as a result of these outages.  Water cannon operation was also restored after each of the outages.  The facility was also placed in primary bypass mode from 1311 to 1715 hours on September 18 after an oily sheen was noted in the separator and in a raceway.  Maintenance personnel later found that “environmentally friendly” fish screen oil entered the system when turbine unit 1 headgates were moved.  The sheen dissipated quickly without any apparent adverse effects on fish or the facility.  
Forebay Debris/Gatewell Debris/Oil: Forebay debris remains light.  Trash rack differentials remained low and no racks were cleaned this week.  Turbine unit 1 gatewell slots remain covered for portable crane work.  The covers prevent intake deck contaminants from entering the gatewell slots.  Gatewell slots 9B, 9C, 10A, and 10B were covered late September 10 in support of T5 transformer replacement.  There are no other problems to report this week other than a slight amount of oil being removed with absorbent pads in slot 10C. 

ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  ESBSs in slots 9C and 11C remain in transducer bypass mode.  Except for the removal of an electrical cable from orifice flow in slot 4A on September 20, all ESBSs operated satisfactorily.  ESBS camera inspections did not occur this week due to the high volume of work on the intake deck.  A comprehensive ESBS inspection is scheduled over the weekend to avoid conflict with intake deck activities on regular workdays.  No VBS cleaning was necessary this week as monitoring efforts all screens met criteria.  The auxiliary hoist for trash raking and the hammer head crane for VBS cleaning remain useable.  The main hoist should return to service in one to three months.  In the meantime portable cranes will be doing all the heavy lifting, and the auxiliary and hammer head hoists (on the main crane) will be used for lighter work.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: For the week, there were 42 orifices opened.  No problems occurred and all channel systems operated well in automatic mode.  The channel was monitored during VBS cleaning activities.  This week, one clipped adult steelhead was lost on the grating at orifice 14C.  A slight tear in the jump netting was quickly repaired.                        

Transportation Facility:  Fish collection for transport continued.  The primary (A and B) PIT tag diversion gates are in service and the secondary (C and D) PIT/bypass gates remain closed and off.  Sample gates operated satisfactorily this week.  All PIT and sample gates were closed during the power outages mentioned above.  On September 21, a leak was noted in a sample raceway truck release line joint.  The leak did not affect the loading operation and the joint was reinforced the next day.  The section will be replaced this winter.  There are no other problems to report.                

Transport Summary:  Trucking operations took place on September 19, 21 and 23, without any difficulties.  On September 22, a fuel line leak on the fish trailer was noted and repaired.      

                                                         River Conditions

River conditions during the week are outlined in Table 1 with data provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Water clarity continues to be provided by the control room.  No spill occurred this week.

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	88.6
	61.4
	0.0
	0.0
	68.4
	67.4
	6.0
	     6.0


*From control room data.

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week. 
Invasive Species:  On September 7, the zebra mussel stations were examined and no mussels were found.  The next inspection is scheduled for October 7.

Predatory bird counts continued with the tailwater and forebay areas being checked twice and once a day, respectively.  The tailwater area had high counts of 37 cormorants and 15 gulls.  Most birds were seen in the spill basin.  No birds were seen at the bypass outfalls.  The water cannon continued to operate well.  No birds were seen in the forebay.  No grebes were noticed at all this week.  The lower than usual bird numbers for this time of year may be related to the unusually low numbers of juvenile shad present.
Project:  Ice Harbor

Biologist:  Mark Plummer 

Technician: Stephen Jeffers
Dates:  September 18 -24, 2009

Turbine Operation
Turbine units 4 and 5 were available for operation throughout this entire reporting period.  Turbine units 1 – 3 were out of service for short periods on September 23 while STS inspections were being performed.  Turbine unit 6 went out of service September 23 to connect an oil purifier.  The turbine unit returned to service on September 24 at 1620 hours.

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways on September 21, 22, and 23.
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. 
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 7.3 feet, on sill with a depth of 7.5 feet, and on sill with a depth of 7.9 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.4 feet, on sill with a depth of 7.6 feet, and on sill with a depth of 7.9 feet.  The north shore entrance (NSE) was on sill with a depth of 7.5 feet, on sill with a depth of 7.6 feet, and on sill with a depth of 8.0 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were within criteria of 1 – 2 feet.  The south and center entrance gates (SFE-1 and NFE-2) are being lowered to reduce entrance velocities to benefit lamprey passage.  This operation began July 20 and occurs between the hours of 2100 hours and 0400 hours and will continue through the end of September.
Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 remains on standby and six of the available eight south fish pumps were operated without any problems.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.
STSs/VBSs:  STS’s are in cycle mode operation.  STS inspections for September are complete.  No problems were found. 

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  20 orifices are open.  The power supply wire system to the screen cleaner in the collection channel continues to have problems.  The juvenile collection channel water elevations and the incline screen area are being monitored by powerhouse operators and fish facility personnel.  The screen cleaner is in manual mode, being run once per day.  Other measures included manual operation of the air burst system and manually raking the accessible portions of the inclined screen.    
Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.    
Removable Spillway Weir:  The RSW was lowered September 22 to test updated software improvements.  The weir was returned to the operating position September 24.  Currently, the weir is not operating due to the end of spill for fish passage.

River Conditions

River conditions during the week are outlined in Table 1.  
Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	21.8
	10.1
	0
	0
	67
	67
	9.7
	9.2


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer gages are read 3 times a reporting period during each adult fishway inspection by fish facility personnel.  The strainers are being visually inspected during STS inspections.  
Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this reporting period.

Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Ken Fone 

Dates:  September 18 -24, 2009

Turbine Operation

Turbine unit 4 was taken out of service for annual maintenance on August 25 at 0715 hours and returned to service on September 22 at 1338 hours.  NERC (North American Electrical Reliability Council) testing was conducted from September 20 through September 22 and caused 14 separate occurrences of operating out of the 1% criteria.  These tests ensure that all equipment and software comply with regional and national electrical generation standards.  Total time outside the 1% criteria was 325 minutes.  The longest time out of criteria by a single turbine unit was 91 minutes and the shortest was 2 minutes.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or state biologists on September 18, 19, 22, and 23.   
Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively).   

Fishway Entrances and Collection Channel: NPE1 and NPE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections with the exception of a reading of 7.9 on September 19.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections, with an average depth of 7.3 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.     

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections, with an average depth of 7.9 feet while on sill.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

Auxiliary Water Supply System: AWS pump 3 remains out of service for bearing housing replacement and diffuser assembly repair.  Pumps 1 and 2 continued in service throughout this period.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.          

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 8.8 square yard of forebay debris observed during this period.  Gatewell debris ranged from 0-13% surface coverage.  No oil was observed in the gatewells.

STSs/VBSs:    STS operation was changed to cycle mode on July 30 as the average fork length of sockeye and chinook juveniles exceeded the 120mm criteria.  STS inspections occurred on September 5 and 6, with no significant problems found.

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass operated with 19 orifices open.  The new orifice lights have an unusually short operating life which is being investigated. The channel, dewatering structure, and flume operated normally.  
Collection Facility:  Fish are being collected for transport.  Equipment is functioning normally. 

Transport Summary:  Alternate day midi-tanker transport began on August 16 and continued through this period.  Salt is being added to the water in the transport tank to achieve a salt concentration of about 2.5 parts per thousand in order to treat fish exhibiting symptoms consistent with columnaris infection.   

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	22.2
	12.4
	0
	0
	67.5
	67
	5+
	4.3


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers: Turbine unit cooling water strainers were cleaned on September 16.  No juvenile lamprey or other fish were present.  This informations will be collected monthly through the year unless degradation of fish due to water temperature makes this task impossible.  

Invasive Species: There were no zebra mussels observed at the monitoring stations on September 3.  The October inspection is expected to occur during the week of October 5.

Project:  Little Goose

Biologist: George Melanson
Dates:  September 18 -24, 2009

Turbine Operation

Turbine units 1, 3 and 4 were available for power generation throughout most of this report period.  Turbine unit 2 was returned to service on September 24 at 0837 hours following completion of scheduled annual maintenance.  All turbine units were removed from service on September 21 at 0605 hours and September 24 at 1812 hours for approximately 30 minutes to disconnect and reconnect transmission line T2.  Turbine units 5 and 6 were removed from service September 21 to 24 to perform repairs to main transformer 2 (T2).  Turbine unit 5 speed-no load operations outside the 1% criteria were necessary to maintain station service on September 24 from 1802 to 1836 hours.  The outage allowed the reconnection of turbine unit 5 to main transformer 2.  Aside from this, all turbines units were operated within 1% efficiency criteria this week.  

Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway on September 18, 19 and 23.

Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged from 1.02 to 1.62 ft. (criteria 1.0 to 2.0 ft.). 

SSE1 and 2 weir depths ranged from 8.24 to 8.38 feet (criteria ≥8.0 ft), NPE1 and 2 weirs rested on sill during the September 18 inspection and depths measured 5.06 and 5.10 feet respectively. NPE1 and 2 weir depths ranged between 7.10 and 7.26 feet (criteria ≥7.0 ft. or on sill) for the remainder of the report period.  NSE1 depths ranged from 6.18 to 6.22 (criteria ≥ 6.0 ft).  NSE2 is raised to approximately 2.5 feet below tail water surface elevation to compensate for water loss through damaged NPE3. 

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 2.1 and 2.9 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.7 and 2.4 fps.
Auxiliary Water Supply System:   Fish pumps were removed from service on September 21 and   24 for approximately 30 minutes each during power outages associated with T2.  Aside from this, all three fish pumps operated within criteria.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Small amounts of debris, less than 100 square feet, were observed inside the trash/shear boom.  Several sticks were removed from gatewell 1A, a plastic bag from 4B and an oil absorbent pad from 6C.  Aside from these, all gatewells remained clear of debris and contaminants this week.  

ESBSs/VBSs: All ESBSs operated within criteria this report period.  Video camera inspections are scheduled for October 6 - 8.

Orifices, Collection Channel, Dewatering Structure, and Flume:  The collection channel operated with 19 open orifices.

The primary dewatering weir motor failed on July 20.  Repairs are on standby - awaiting parts.  The weirs are being manually operated to regulate water flow volume into the bypass flume.

Transportation Facility:  The facility was without power on September 21 and 24 for approximately 30 minutes each during power outages associated with transformer T2. The outages did not interfere with the transportation facility operations.  A total of 85 salmonid smolts were collected this week.  Descaling was not observed.  A total of 5 smolt mortalities were incurred during this report period.  All mortalities appear to be disease (presumed columnaris) related.   

Transport Summary:  Alternate day truck transport operations using the 300-gallon midi tank continued this week.  Salt in small concentrations of approximately 1 g/L is added to the midi-tank water to treat potential Columnaris disease and reduce stress.  All truck loading and transport operations were performed satisfactorily.
Spillway Weir:  Spillway Spillway 1 and the TSW operations ceased with the cessation of summer spill on August 31. 
River Conditions
River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	   23.4
	12.2
	0.2
	0
	66.8
	66.4
	6.0
	5.6


*Ladder temperature.
Spill occurred on September 21 and 24 during turbine unit shutdowns associated with transformer T2 repairs. 

Other
Inline Cooling Water Strainers:  Cooling water strainers associated with turbine units 1 through 6 were inspected on September 22 - no fish or fish remains were observed. 

Invasive Species:  The zebra mussel substrate was inspected on September 2.  No mussels were observed.   The next inspection is scheduled for October 5.

Up to 16 gulls and 12 cormorants were observed in vicinity of the dam during the report period.   

Project:  Lower Granite

Biologists: Mike Halter and Casey Watson
Dates:  September 18 -24, 2009

Turbine Operation

Lower Granite had turbine units 1, 2, 3, 4, and 6 available for power generation at the beginning of the report week. Turbine unit 5 was put back in service on September 22 and was available for the remainder of the report week. 
Adult Fish Passage Facility

On September 21 and 25, the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.
Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were within criteria whenever the tailwater depths were sufficient to keep the gates off their sills (at tailwater elevations below 633.0 feet the south shore gates bottom out).  Weir depths at the south shore entrances ranged between 7.9 and 8.0 feet during the weekly inspections (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse fishway entrances were below the desired 8.0 foot criteria level on all inspections this week due to low tailwater elevations which caused the gates to bottom out and rest on their sills (at elevations below 636.0 feet the north powerhouse gates bottom out).  North powerhouse entrance weir depths ranged from 6.9 to 8.0 feet.  Weir depth readings at the north shore fishway entrances were out of criteria all week and ranged between 5.0 and 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.91 to 1.05 feet per second and averaged 0.91 feet per second.

Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.  
Juvenile Fish Passage Facility
The facility sample rate remained at 100% during the report week.

Forebay Debris/Gatewell Debris/Oil:  Debris levels were moderate to heavy during the week. There were no plugging issues of any kind. Increasing reservoir levels are returning large amounts of woody debris to the river from areas where it was deposited during spring flows.

ESBSs/VBSs: The last VBS/ESBS inspections took place on August 21-23.  The next inspections are scheduled for late September or early October.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  As a fail-safe measure, collection gallery orifices continued to be backflushed every three hours throughout the week.
Transportation Facility:  The facility remained at a 100% sample rate during the week.  Fish were worked up in the lab every other day and transported to the truck pad below Bonneville Dam and released into to bypass outfall pipe.
Transport Summary:  Fish trucking operations to Bonneville Dam continued during the week.  Due to low fish numbers and a 100% sample rate, the midi-tanker was used for all trucking operations this week. All operations proceeded smoothly.
Removable Spillway Weir:  Nothing to report on the RSW.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	25.2
	14.8
	0.0
	0.0
	69
	68
	5.0
	5.0


*Scrollcase temperature.

Other
Inline Cooling Water Strainers:   Inline cooling water strainers on turbine unit 5 were checked for lamprey on September 23. No evidence of live or dead lamprey was sighted.
Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on August 31.

Adult Fish Trap: Adult fish trap operations continue at a sample rate of 9%. A total of 5,000 unclipped (wild) steelhead are to be PIT-tagged for Idaho Fish and Game.

