U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#41-2009
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  December 4 - 10, 2009

Turbine Operation

McNary had 13 turbine units available for power generation during this report period.  Turbine unit 4 remains out of service for 9-year overhaul, and is expected to return to service next week.  Troubles with transmission line 6 on December 7 forced turbine units 11 and 12 out of service for 7 hours.  Because the remaining turbine units in operation assumed the overall electrical load, high VBS differentials were measured during this 7 hour period.  Once turbine units 11 and 12 and transmission line 6 returned to service, the electrical load by individual turbine units dropped as did VBS differentials.  Electrical load reductions became necessary in turbine units 1, 2 and 3 on December 9 and turbine unit 5 on December 10 as VBS differentials exceeded criteria. Affected VBSs are scheduled to be cleaned December 11 and 12 when the intake deck crane is expected to be available for service.  The soft one percent turbine efficiency constraint was met this week except during the transmission line 6 outage mentioned above.  Severe winter weather made for hazardous work conditions through most of this report period.  
Adult Fish Passage Facilities

On December 5, 8 and 10, the McNary fisheries biologists performed measured inspections of the adult fishways.  
The Washington ladder was inspected only once this week as the ladder was placed in orifice flow mode on December 6 at 0837 hours in preparation for winter maintenance.  Entrance bulkheads were installed in the Washington ladder on December 7 and 8, followed by exit stop log installations on December 9.  Prior to stop log installations, the flow down the ladder was directed through the bypass/energy dissipater as the PUD turbine unit was previously taken out of service on December 7.  The diffuser gratings were examined by camera and no problems were found.  Dry ladder inspections revealed two orifices partially blocked by woody debris (debris subsequently removed) and a lower duplex PIT tag antenna in need of repair (which will occur early next week).  Ten adult shad and one residual steelhead smolt were evacuated to the lower pool during the dewatering operation.  On December 10, ponded fish were evacuated from the tilting weir area with 40 shad and one crappie being removed.  The ponds form as the weirs are mounted on concrete stub walls.  The tilting weir section of the ladder was found in good condition.  Sensor stilling wells will be cleaned before the ladder returns to operation on approximately December 17.  On December 9, from 1040 to 1233 hours, the Oregon ladder was placed in orifice flow mode so the exits could be examined for potential modifications for adult lamprey passage.               
Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections except on December 5 when the head over weir differential measured 1.6 feet in the Washington ladder.  Operators immediately adjusted the weirs to maintain criteria.  The exit weir remained in manual operation for electrical upgrades until December 6 when the ladder was placed in orifice flow mode in preparation for winter maintenance.  The Oregon ladder exit weir triggered alarms twice this week, once on December 4 and once on December 10.  In both cases, normal operation resumed after the alarm was reset.  The exit traveling screens remain out of service for maintenance and to prevent ice damage to the system.  On December 7, divers closed two unwatering sump drain valves on the downstream side of the traveling screens.  This action will help facilitate screen repairs.             
Fishway Entrances and Collection Channel:  All Washington ladder inspection points were in criteria prior to shutdown for winter maintenance.  All Oregon ladder inspection points were also in criteria except for the north pool differential which measured 0.6 to 0.7 feet all week.  The pool differential readings were influenced by the juvenile system being in emergency bypass (see below) and by the closure of the 1,000 cfs gravity fed conduit (traveling screens are out of service).  No collection channel velocity measurements were taken this week.      
Auxiliary Water Supply System: All three fish pumps operated this week with blade angles of 22 to 30 degrees with no problems to report.  The 1000 cfs supply conduit was closed for the season on December 3 to prevent freeze damage.  The juvenile facility was previously switched from primary to emergency bypass mode on December 3.  The Wasco County PUD unit operated well until it was removed from service at 0801 hours on December 7 for winter maintenance along with the Washington ladder.     

Juvenile Fish Passage Facility

On December 3, the primary bypass season concluded with the switch to emergency bypass in anticipation of severe winter weather and for winter maintenance preparation.  The system will remain in emergency bypass until the ESBSs are raised for maintenance in mid to late December, at which time the collection channel orifices will be closed. 

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains light.  No trash racks were cleaned this week as differentials remained low.  Slots 9B, 9C, 10A, 10B, 14A, 14B and 14C remain covered in support of main hoist work on the intake deck crane and for portable crane parking.  The covers help keep contaminants from entering the intake slots.  No problems were observed during this report period.  On December 14, the main hoist on the intake deck crane will be load tested.  There were no problems to report other than a slight sheen of oil that was removed from slot 4A slot with absorbent pads.
ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  The screens in slots 9C and 11C remain in transducer bypass mode.  ESBS camera inspections did not occur this week as the screens will be raised and examined in the near future.  VBS monitoring revealed twelve differential readings out of criteria on December 7 due to high turbine unit electrical loads.  Once loads were reduced the differential measurements met criteria.  These readings did indicate that debris accumulations were evident as 6 VBSs in turbines units 1 through 3 and 5 measured out of differential criteria on December 9 and 10.  All turbine units were being operated within one percent efficiency criteria operating criteria at the time.  These and eight other screens will be cleaned on December 11 and 12.  Eleven of the 12 screens measured on December 7 are scheduled to be cleaned.  

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, there were 42 orifices opened.  No problems occurred and all channel systems are out of service for winter maintenance.                                         

Transportation Facility:  Emergency bypass operations continued.  The facility was previously dewatered and winterized.  Winter maintenance season continues.                     
Transport Summary:  There is nothing to report.  

River Conditions

River conditions during the week are outlined in Table 1 with data provided by the control room whose data day runs from 0000 to 2400 hours.  Scheduled maintenance on spillbay hoists continues.     

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	    151.4
	104.0
	0.0
	0.0
	48.0
	45.0
	6.0
	     6.0


Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week. 
Invasive Species:  On November 14, the zebra mussel stations were examined and no mussels were found.  The next the zebra mussel inspection will occur on December 14.        

During casual observations, gulls and cormorants were noted feeding and roosting in the tailrace near the powerhouse.  Some birds were also noted at the emergency bypass outfall.  Only an occasional gull, cormorant or grebe was observed in forebay locations.  No grebes were observed within the bypass system.  Bird numbers appear to be fluctuating with the juvenile shad out migration.  

Project:  Ice Harbor

Biologist:  Mark Plummer 

Technician: Stephen Jeffers
Dates:  December 4 - 10, 2009

Turbine Operation
Turbine units 2, 4, 5, and 6 were available for operation this entire reporting period.  Turbine unit 3 was unavailable December 8 due to loss of governor control and came back online December 9.  Turbine unit 1 remains out of service for overhaul.

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways on December 4, 7, and 9.
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north shore adult fish ladder is tentatively scheduled to be unwatered to tailwater elevation for annual maintenance and inspection from January 4 to January 14.   The south shore adult fish ladder is tentatively scheduled to be unwatered completely for annual maintenance and inspection from January 19 to February 25.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 6.8 feet, on sill with a depth of 8.4 feet, and on sill with a depth of 7.3 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 6.8 feet, on sill with a depth of 8.3 feet, and on sill with a depth of 7.3 feet.  The north shore entrance (NSE) was on sill with a depth of 6.9 feet, on sill with a depth of 8.4 feet, and on sill with a depth of 6.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All Channel/Tailwater differentials were within criteria of 1 – 2 feet.
Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 is on standby.  All 8 south fish pumps are available for operation.  Currently, 6 of the available 8 south fish pumps were operated without problems.  North shore fish pump 3 will be out of service beginning December 14 to diagnose and correct a small oil leak thought to be located around the pump shaft.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.
STSs/VBSs:  STSs are in cycle mode operation.  Turbine unit 1 STS’s were raised December 3.  The remaining STS’s are tentatively scheduled to be raised for winter maintenance from December 16 to December 17.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.  The power supply system to the JFF screen cleaner which is located in the juvenile collection channel, continues to have problems. Due to the hazards of working over the operating juvenile fish channel, permanent repairs will be made when the channel is unwatered during the winter maintenance period.  The dewatering screen is being monitored and manually cleaned.
Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.  Approximately 270 cfs is dewatered and directed into the south adult fish ladder for adult attraction water leaving 30 cfs for adult fall backs and juvenile fish transportation through the bypass.  The juvenile fish bypass is tentatively scheduled to be unwatered for winter maintenance on December 17.

Removable Spillway Weir:  The RSW weir is in the deployed position.  Currently, the RSW weir is not in operation as spill for fish passage ended August 31.

River Conditions

River conditions during the week are outlined in Table 1.  
Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	20.0
	13.1
	0
	0
	47
	44
	7.8
	7.2


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer pressures are recorded 3 times a reporting period during each adult fishway inspection performed by fish facility personnel.

Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this reporting period.

Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Ken Fone 

Dates:  December 4 - 10, 2009

Turbine Operation

All turbine units were operated within the 1% operation criteria.  Turbine unit 3 previously taken out of service for annual maintenance on November 2 at 0700 hours was returned to service December 10 at 0830 hours.  Turbine unit 5 was taken out of service for annual maintenance on November 30 at 0700 hours and remained out of service through this report period. 

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on December 7, 8 and 10.   
Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively).   

Fishway Entrances and Collection Channel: NPE1 and NPE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections with the exception of the December 10 inspection which had a 7.9’ reading.  This discrepency would likely have little or no adverse effect on fish passage.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE1 and SPE2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections, with an average on sill depth of 7.4 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.     

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

Auxiliary Water Supply System: AWS pump 3 remains out of service for bearing housing replacement and diffuser assembly repair.   Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.                    

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 156.3 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0 - 21% surface coverage.  No oil was observed in the gatewells.  Strong winds coming from the east destroyed the debris booms at the north and south ladder exits.  Temporary booms have been installed.
STSs/VBSs:  STS operation was changed to cycle mode on July 30 when the average fork length of sockeye and chinook juveniles exceeded the 120mm criteria.  November STS inspections were conducted on November 2 and 3.  The STS in slot 2C failed inspection due to missing cross bars.  The damaged screen was replaced the same day.  All other STSs were operable.  STSs will be raised for winter maintenance on December 16 and 17.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass operated with 18 orifices open.  The new orifice lights have an unusually short operating life which is being investigated.  The channel, dewatering structure, and flume operated normally.  
Collection Facility:  The facilities were placed in primary bypass mode on October 1 at 0700 hours.  

Transport Summary:  Transport ended October 1.   

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	20.6
	12.6
	0
	0
	43.0
	41.5
	5+
	5+


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers: Turbine unit cooling water strainers were checked on December 3.  Fish were not counted as fisheries personnel were unavailable.  

Invasive Species: There were no zebra mussels observed at the monitoring stations on December 3.  

Due to reports of upcoming freezing weather, the bird aversion sprinklers were shut off on December 3.

The navigation lock was out of service from December 4 at 1000 hours to December 9 at 1730 hours.  Extensive work will be done on the lock this winter.

.  
Project:  Little Goose

Biologist: Rick Weis
Dates:  December 4 - 10, 2009

Turbine Operation

Turbine units 1, 3, 4, and 6 were available for power generation throughout this report period. Turbine unit 2 was forced out of service on October 1 due to thrust oil pump failure - repairs are ongoing. Turbine unit 5 was returned to service on Dec. 10.  All available turbine units operated within 1% efficiency criteria this week.  

Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on Dec. 7, 9 and 10.

Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged from 1.20 to 1.56 feet near the SSE; 1.12 to 1.18 feet near the NPE1 and 0.88 to 1.16 feet near the NSE (criteria 1.0 to 2.0 ft.). Fish pump rpms were increased to return NSE to criteria. 

SSE1 and 2 weir depths ranged from 8.26 to 8.40 feet (criteria ≥8.0 ft).  NPE1 and 2 weir depths ranged between 6.88 (sill) and 7.24 feet (criteria ≥7.0 ft. or on sill).  NSE1 weir previously broke free after cable and control system failure and is resting on sill at 529.0 ft. (criteria ≥ 6.0 ft or on sill).  NSE2 was completely raised and closed off on November 16 at 0940 hours to compensate for water loss through damaged NPE3 and NSE1.  

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 2.9 and 3.3 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.2 and 2.6 (criteria 1.5 to 4.0 fps).

The adult fish collection channel was temporarily shut down for ROV (remotely operated vehicle) inspection on Dec. 8.  Fish pumps were shut off and NPE weirs were raised.  The inspection started at 0900 hours and lasted until 1200 hours when pumps and weirs were placed back into normal operating range.

Auxiliary Water Supply System: All three fish pumps operated within criteria except during the ROV inspection on Dec. 8 when the three pumps were shut off to decrease flows in the adult collection channel. 

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil: Forebay debris remained minimal.  Gatewells for the most part remained clear of debris and contaminants.

ESBSs/VBSs: Manual cycling of the ESBS cleaning brush in slot 1C continued.  All ESBSs were operated within criteria this report period.   

Orifices, Collection Channel, Dewatering Structure, and Flume: The collection channel operated satisfactorily with 19 open orifices.      

Transportation Facility: Operations at the facility were switched to primary bypass mode on October 31.  The water supply/emergency bypass pipe and the facility were dewatered on November 3.  No problems to report – winter maintenance has begun.

Transport Summary:  Transport operations ended October 31.  

Spillway Weir:  Spillway 1 and the TSW were removed from service on August 31. 
River Conditions
River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	   17.4
	10.7
	0
	0
	43.1
	41.4
	6.0+
	6.0


*Ladder temperature.
Other
Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week.     

Invasive Species:  The Zebra Mussel substrate was inspected on December 14.  No mussels were observed.   The next inspection is scheduled for January 16.

Up to 36 gulls and 6 cormorants were observed in the vicinity of the dam during the report period.   The increase in bird numbers over the past several weeks is in response to the juvenile shad outmigration.  

Project:  Lower Granite

Biologist: Mike Halter
Dates:  December 4 - 10, 2009

Turbine Operation
Lower Granite had turbine units 1, 2, 4, 5 and 6 available for power generation at the beginning of the report week.  Turbine unit 3 remained out of service during the week due to failed exciter brushes.  It is scheduled to return to service by December 31.  All operating turbine units were run within the established 1% efficiency guidelines. 

Adult Fish Passage Facility

On December 7, 8, 9 and 10 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.   
Fish Ladder:  All criteria were met during the week.
Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore entrances also remained within criteria on all inspections. Weir depths at the north powerhouse entrances met criteria whenever the tailwater elevation was in excess of 636.0 feet (the level at which the gates bottom out and rest on their sills).  The only exception was on the December 9 inspection when gate NPE-1 was found out of the water.  This was reported to the operator and the gate was adjusted and brought down to the proper level.  Weir depths at the north shore fishway entrances were below criteria on all inspections this week and ranged from 5.0 to 5.2 feet (criterion ≥ 7.0 feet). Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential. Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.77 to 1.06 feet per second and averaged 0.91 feet per second.

Auxiliary Water Supply System: Fish pumps 1 and 3 were operated throughout the week without any problems.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris levels were light during the week. There were no plugging issues of any kind.

ESBSs/VBSs:  The last video inspections of the year took place on October 23 and 24.  A small hole was detected on the VBS in slot 1A approximately 3 feet down.  No other problems were detected.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  As a fail-safe measure, collection gallery orifices were back-flushed every three hours.  Debris accumulations dropped off to very low levels this week.
Transportation Facility:  Fish collection and transportation activities concluded for the season when the system was switched to secondary bypass mode on October 31.  Juvenile fish were then routed over the separator for PIT-tag monitoring purposes.  PIT-tag monitoring of juvenile fish was suspended at 1200 hours on December 5 when the separator was placed into primary bypass mode (fish diverted out the large pipe at the base of the separator) due to very cold temperatures and fear of frost damage to the facility pipes.  The bypass of fish in this manner is expected to continue until the planned suspension of juvenile fish operations on December 16 due to continued cold temperatures.
Transport Summary: Nothing to report.  Fish transportation activities have concluded for the season.
Removable Spillway Weir: Work was conducted during the week on the control mechanisms that regulate lowering the structure to the pad on the river bottom.

River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	19.1
	12.4
	0.0
	0.0
	44.9
	43.2
	5.0
	5.0


*Scrollcase temperature.

Other
Inline Cooling Water Strainers:   Inline cooling water strainers in turbine unit 3 were checked for lamprey on September 28.  No evidence of live or dead lamprey was sighted.
Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on November 12.

Adult Fish Trap:  The adult fish trap complex remains dewatered for the winter season.
