
U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#05-2010
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  March 26 – April 1, 2010.
Turbine Operation

McNary had 13 to 14 turbine units available for power generation this week.  From March 29 to 30, turbine unit 6 was taken out of service in support of experimental orifice lighting installation (see below for details).  On April 1, turbine units 1 through 3, 5, and 7 through 9 were alternately taken out of service for trash rack cleaning.  Cumulative outage time totaled 8.7 hours.  The hard one percent constraint criteria began April 1.  No turbine units operated outside either the soft or hard 1% criterion this week.      

Adult Fish Passage Facilities

On March 26, 28 and 30, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts resumed April 1 as scheduled.  The picketed leads were previously lowered March 23.  The north Oregon ladder exit traveling screen was returned to service on April 1.  This operation required a 2 hour closure of the Oregon ladder 1000 cfs conduit so the north traveling screen bulkheads could be removed.  
Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  As mentioned above, the north Oregon exit traveling screen returned to service on April 1.  The south Oregon exit traveling screen continues to operate well and differential monitoring revealed no problems.  
Fishway Entrances and Collection Channel:  All Washington ladder and most Oregon ladder inspection points were in criteria.  The Oregon ladder north powerhouse pool differential respectively measured 0.8 and 0.7 feet on March 26 and 28.  On March 30, NFEW2 and NFEW3 weir depths measured 8.9 and 8.8 feet respectively.  Readings should improve next week as the juvenile bypass system is now discharging excess water into this adult fishway.  All other Oregon inspection points were in criteria.  Collection channel velocities averaged 1.2 feet per second.    

Auxiliary Water Supply System:  For the week, all three fish pumps ran with blade angles of 22 to 28 degrees with no interruptions in service.  As mentioned above, the Oregon supply conduit was briefly closed on April 1.  As mentioned above, the juvenile facility began supplying 450 cfs to the north powerhouse pool on April 1.  The Wasco County PUD turbine unit had no interruptions in service during this report period. 

Juvenile Fish Passage Facility

With the completion of winter maintenance on March 31, the juvenile bypass system was watered up briefly between 1235 and 1600 hours, and switched from emergency to primary bypass mode.  However, due to a leaking slip joint in the transition between the full flow pipe and the rectangular flume, the primary bypass was subsequently dewatered.  The slip joint or dresser coupling had moved approximately six inches, causing the leakage.  This was most likely caused by repeated heat expansion/contraction and/or wind vibrations over the years.  Following shutdown, one adult steelhead, two sockeye smolts, one Chinook smolt and one steelhead smolt were salvaged from the channel and returned to the forebay without any complications.  On April 1, the maintenance crews repaired the dresser coupling which resealed the gasket.  The full flow pipe was again watered up between 1400 and 1600 hours and switched to primary bypass without incident.  Primary bypass will continue until April 5 when primary bypass operations will alternate with secondary bypass operations every other day.  ESBSs installations will also begin April 5.  Collection for the first 24 hour sample will begin April 6.  The first sample results will become available April 7.

Forebay Debris/Gatewell Debris/Oil: Forebay debris remains light with some of the debris in the area around the Oregon ladder exit.  On April 1, some floating debris was removed along with trash raked from racks associated with turbine units 1 through 3, 5 and 7 through 9.  Approximately 7 ten-yard truck loads of debris were removed.  The debris consisted mostly of tumbleweeds and wood.  A large log was also removed.  Slight amounts of residual fish screen oil were noted in 3 gatewell slots, all of which was removed with absorbent pads.  From March 29 to 30, gatewell slot 6B was dewatered for installation of an experimental orifice light-ring.  The equipment is to be used in an upcoming orifice lighting study. 

ESBSs/VBSs:  ESBSs remain raised and maintenance is almost complete.  VBS monitoring will resume when fish screen installations begin.  ESBS installations are slated to take place between April 5 and April 15.  As in 2009, ESBSs are being deployed one to two weeks later than previous years as a juvenile lamprey protection measure.  

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  During primary bypass operations, 42 orifices were in service.  All systems operated well in automatic mode.  On April 1, facility personnel noted that an extreme high water collection channel alarm had been triggered although the alarm in the control room appeared to be functioning properly.  Electrical staff will attempt to resolve this issue on the next work day (following the close of this report period).  Since the facility personnel are monitoring the collection channel 24 hours per day during primary bypass operations, there should be no problems.  Electricians also completed orifice attraction lighting work by finishing the box cover installation on April 1.  As mentioned above, the bypass pipe joint was also repaired on April 1. 

Transportation Facility:  After completion of all repairs and winter maintenance prior to March 31, the facility was “watered up” during primary bypass operations as described above.  The PIT and sample systems were tested and functioned well when in primary bypass mode.  The facility will remain out of service until April 6, the first scheduled day of secondary bypass operations.  No problems were observed.                         

Transport Summary:  No transport operations took place this week. 

River Conditions

River conditions during the week are outlined in Table 1 as provide by control room data, which runs from 0000 to 2400 hours each day.  Starting next week, Table 1 data will be provided by the smolt monitoring staff utilizing a reporting period running from 0700 to 0700 hours each day.  Spillway gate rehabilitation and testing is almost complete.  Spring spillway operations are slated to begin April 10.   

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	112.4
	83.4
	0.0
	0.0
	46
	45
	6.0
	     5.6


*Unit 1’s scroll case temperature.

Other

Inline Cooling Water Strainers:  No cooling water strainers were inspected this week.  The next inspection is expected to take place in 2 weeks. 
Invasive Species: The zebra mussel detection stations were inspected March 5, none were found.  The next inspection is expected to take place on April 5.  Large numbers of exotic juvenile shrimp were noted while personnel were examining the travelling screens at the Oregon ladder exit this week. 

Bird counts resumed March 28, when the technicians returned to shift work.  Tailwater counts and forebay observations are being performed twice and once daily, respectively.  Only an occasional gull, cormorant, pelican, grebe or osprey was observed.  No significant numbers of birds were reported.  On April 1, the water cannon became operational.  
APHIS personnel are slated to begin hazing duties April 5.  
Preparations for research studies continued.                 

Project:  Ice Harbor

Biologist:  Mark Plummer 

Dates:  March 26 – April 1, 2010.

Turbine Operation
All turbine units (1 - 6) were available for operation this reporting period.  No problems to report.

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways March 26, 29, 30, 31, and April 1. 
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria, except March 29, 30, 31, and April 1.   On these inspections, the south upper fish ladder diffuser staff gage indication varied from 0.8 feet to 0.9 feet (criteria is 1.0 – 1.3 feet).  The diffuser valve can not be operated in automatic mode to adjust for more water.  Maintenance believes the problem is with the diffuser valve.  Valve repairs would require unwatering the upper south adult fish ladder.  Manually operating the valve could cause the valve to fail entirely.  Since adult spring Chinook are expected to arrive in the near future, project personnel decided to leave valve in the current configuration.  The north and south fish ladder picketed leads are in their lowered position for counting.  Adult fish counts began April 1. 

Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 8.1 feet, on sill with a depth of 7.5 feet, off sill with a depth of 8.4 feet, off sill with a depth of 8.2 feet, and off sill with a depth of 8.0 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 8.1 feet, on sill with a depth of 7.5 feet, off sill with a depth of 7.9 feet, off sill with a depth of 9.1 feet, and off sill with a depth of 8.3 feet.  The north shore entrance (NSE) was off sill with a depth of 7.7 feet, off sill with a depth of 6.9 feet, off sill with a depth of 7.7 feet, off sill with a depth of 7.7 feet, and off sill with a depth of 7.5 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All out of criteria events were identified to the powerhouse shift operator for correction.  All channel/tailwater differentials were in criteria, except for March 29 and 31.  On these inspections, the powerhouse shift operator was notified to make necessary adjustments.  Channel/tailwater differential criteria are 1 – 2 feet.
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without any problems.  All north shore fish pump are in service.  Six of the 7 available south fish pumps were operated.  The remaining south fish pump (#4) is out of service due to gearbox problems. 

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay in front of the powerhouse.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  

STSs/VBSs:  The STSs are in cycle run timing mode.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.  
Juvenile Bypass Facility:  The bypass was put in operation March 8.

Juvenile Fish Sampling:  The first sample is scheduled for Tuesday, April 6 to allow more personnel to observe the new anesthetic re-circulation system in operation.  Regularly scheduled sampling days have changed to Mondays and Thursdays.

Removable Spillway Weir:  The RSW is in the deployed position, ready for service.
River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	41.0
	20.1
	0.0
	0.0
	45
	44
	6.8
	6.2


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week. 
Invasive Species:  No zebra mussel inspections were performed this week.     
The temporary high velocity experimental separator at Ice Harbor Fish Facility was removed during the winter maintenance season.
An anesthetic re-circulation system has been installed for use this season.
Spill for fish passage will begin April 3.
Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Elizabeth Lindsey 

Dates:  March 26 – April 1, 2010.

Turbine Operation

All turbine units were operated within the soft constraint of the 1% operation criteria until April 1 when the hard constraint criteria began.  Hard 1% constraint requirements were met on April 1.  There were no turbine unit outages this week. 
Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on March 28, 29, 31, and April 1. 

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE 1 and SPE 2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 6.8’, 7.6’, and 7.8 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) this week.    

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth reading was 7.6 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Auxiliary Water Supply System: AWS pump 3 has been out of service to replace the bearing housing and for diffuser assembly repairs.  This work is scheduled to be completed in 2010.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.   

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 53 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-20% surface coverage.  No oil was observed in gatewells.
STSs/VBSs:  STSs were installed on March 23 and 24 and are operating in cycle mode.      

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass is in service with 19 orifices open. 
Collection Facility:  The facility was “watered up” for testing on March 30.  Collection of fish for condition monitoring began on April 1. 
Transport Summary:  The facility is not collecting fish for transport at this time.  

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	38.7
	19.8
	0
	0
	46.2
	46.0
	5.0
	5.0


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers: Turbine unit cooling water strainers were cleaned on March 31.  The contents included the following aquatic organisms.  All were deceased.

Turbine unit 1:  S. Prawn (1), Lamprey (1)

Turbine unit 2:  (0)

Turbine unit 3:  Lamprey (3)

Turbine unit 4:  (0)

Turbine unit 5:  S. Prawn (2), Lamprey (9)

Turbine unit 6:  S. Prawn (2), Lamprey (1), Crappie (1)

Invasive Species: There were no zebra mussels observed at the monitoring stations during the March 9 inspection.

Project:  Little Goose

Biologist: George Melanson
Dates:  March 26 – April 1, 2010.

Turbine Operation

Turbine units 1 through 6 were available for service throughout most of this report period.  Turbine unit 5 was removed from service on March 29 from 0705 to 1425 hours in support of ESBS installations.  Turbine unit 6 was removed from of service on April 1 at 0001 hours due to delayed installation of ESBS.  All turbine units were operated within 1% of best efficiency criteria. 
Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway March 29, 30 and April 1.
Adult fish counts resumed April 1. 

Fish Ladder:  The ladder exit head differentials measured between 0 and 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs held steady at 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady a 0.0 feet (criteria < 0.3 ft.).  

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.26 and 1.76 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.18 and 8.30 feet (criteria ≥8.0 ft), NPE1 weir is manually positioned on sill and depths measured between 6.42 and 7.18 feet (criteria ≥7.0 ft. or on sill). NPE2 weir depths ranged between 6.38 (sill) and 7.14 feet (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 532.5 feet and depths measured between 5.90 and 6.70 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.14 and 6.18 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.5 and 2.0 fps near the SSE and 1.8 to 1.9 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 0.8 and 1.1 fps.  

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris inside the trash-share boom held steady at approximately 3,000 square feet.  Approximately 2 yards of debris was removed from gatewells 5A – 5C after ESBS deployments.

Spillway Weir:  The spillway weir was not operated during this report period.
ESBS/VBS:  ESBS associated with turbine unit 5 were lowered into position on March 29.  All operating ESBSs were within criteria this report period.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection channel is service with 21 open orifices.  
Transportation Facility:  The juvenile fish collection and transportation facility was watered up on March 31.
Transport Summary:  Transport operations are expected to begin in late April or early May. 
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	34.2
	21.8
	0
	0
	47.1
	46.5
	6.0
	5.2


*Ladder temperature.

Other

Cooling Water Strainers:  The next inspection of the cooling water strainers is scheduled for April 7.

Invasive Species:  The next inspection for zebra mussels is scheduled for April 21.  

Avian Activity: The occasional gull was observed this report period.
Project:  Lower Granite

Biologist: Mike Halter
Dates:  March 26 – April 1, 2010.

Turbine Operation

Lower Granite had turbine units 1, 2, 4, 5, and 6 available for power generation at the beginning of the report week.   Turbine unit 3 is out of service for a rewind and will not be available until approximately December of 2010.
Adult Fish Passage Facility

On March 26, 27, and 29 the Lower Granite fisheries biologist performed measured inspections of the adult fishway system.
Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at south shore fishway entrance two were also within criteria on all inspections this week.  The weir depth on south shore fishway entrance one was slightly out of criteria on the March 26 inspection with a depth of 7.9 feet (criterion ≥ 8.0 feet) but returned to within criteria on the following two inspections.  Both north powerhouse fishway entrances remained on sill during the week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 4.9 to 5.5 feet. Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 4.8 and 5.1 feet on both gates (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.88 to 0.99 feet per second and averaged 0.93 feet per second.

Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.
Juvenile Fish Passage Facility

The first daily sample was processed on March 26 – no juvenile salmonids were present.  Consequently, the sample rate was increased from 10% to 20% that morning in an attempt to collect a few fish in the sample the following day.  A total of 5 juveniles (2 non-clipped chinook, 3 non-clipped steelhead) were processed in the March 27 sample.  Juvenile fish numbers remained very low in the daily sample during the week and consequently the sample rate remained at 20% through the duration of the report week.  All fish (other than those being sampled) are being bypassed back to the river through the long outflow pipe (secondary bypass).

 Forebay Debris/Gatewell Debris/Oil:  Forebay debris was minimal and none was removed this week.  Trash was raked from all turbine units in late February.
ESBSs/VBSs:   There were no problems with fish screens during the report week.  ESBS video inspections are scheduled for April 23-25.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Orifices are being backflushed every three hours to ensure they remain free of materials that might impact fish passage.
Transportation Facility:  General transport operation plans are uncertain at this time but could start earlier than recent years due to the low flow forecast.  The first research barge is slated to leave Lower Granite on April 8.
Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	35.4
	22.2
	0.2
	0.0
	48.9
	46.4
	5.0
	5.0


*Scrollcase temperature.

Other
Cooling Water Strainers:  Cooling water strainers were last checked on March 15.

Invasive Species:  No zebra mussels were observed this week.  

Visual counting operations at the adult fish viewing window began on April 1.  The counting hours are from 0400 to 2000 hours.  This operation will continue through October 31.
Adult fish trap operations continued with a sample rate of 15%.  Wild steelhead are being PIT-tagged and genetic and scale samples are being taken.  In addition, scale samples are being taken from one out of every 25 hatchery steelhead. 
