
U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#08-2010
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  April 16 - 22, 2010
Turbine Operation

McNary had 12 turbine units available for power generation for this report period.  Turbine units 2 and 7 remain out of service for asbestos removal.  On April 21, turbine unit 6 was taken out of service for 4.5 hours to allow hub tapping.  No turbine units operated outside the 1% efficiency criterion this week.
Adult Fish Passage Facilities

On April 16, 18 and 20, McNary fisheries biologists performed measured inspections of the adult fishways.  Adult fish counts continued.    

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during inspections.  The Washington ladder tilting weir 338 triggered an alarm once this week.  Normal operation resumed after the alarm was reset.  The Oregon exit traveling screen wash pump also triggered one alarm this week.  Normal operation was restored after the alarm was reset.  Differential readings at the Oregon exit traveling screens were satisfactory. 

Fishway Entrances and Collection Channel:  All Washington ladder inspection points were in criteria.  All Oregon ladder inspection points were in criteria except for north powerhouse pool differentials on April 18 and 20.  The differential measured 0.9 feet on both dates.  Collection channel velocities averaged 1.3 feet per second.    

Auxiliary Water Supply System:  All three fish pumps ran with blade angles of approximately 28 degrees without any interruptions in service.  The juvenile facility continues to add 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no interruptions in service during this report period.

Juvenile Fish Passage Facility

Alternate days of primary and secondary bypass operations continued, with the switch between bypass modes occurring each morning at 0700 hours.  No deviations from this schedule occurred this week.  For this report period, 7,265 smolts were routed to the tailrace during secondary bypass operations.  Starting April 27, extra sampling and smolt collection will be conducted on one or two days per week in support of research.    

Forebay Debris/Gate well Debris/Oil:  Forebay debris accumulations were light.  Wind has been dispersing incoming floating debris, including tumbleweeds.  Trash rack cleaning will resume next week.  No problems were observed in the gatewell slots.        

ESBSs/VBSs:  ESBSs are currently deployed in all turbine units except for those in turbine units 2 and 7.  As mentioned above, these two turbine units are out of service for asbestos removal.  The screen at 5C slot remains in transducer bypass mode.  The ESBS in slot 14C was returned to automatic mode on April 19.  Screens in slots 9A and 9C were placed in bypass mode after tripping alarms on April 22.  Screens in slots 12A and 14A were found to be cycling too often (respectively on April 18 and 16).  Normal operations resumed in both cases after cycling times were adjusted and reset.  On April 19, one spare ESBS was moved from the storage yard to the intake deck.  ESBS camera inspections should resume in May.  VBS monitoring revealed no problems.  VBS differential readings will likely change with expected increases in spring river flows.             

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, 42 orifices were in use and no obstructions were noted.  All systems operated well in automatic mode with two exceptions.   On April 21, the rectangular screen cleaning device triggered a timing alarm.  Debris appeared to have jammed the mechanism as the brush was lowering.  Stoppage occurred just before the brush was to begin traveling downstream.  The biologist successfully operated the brush manually before returning it to automatic operation.  Electricians subsequently checked the limit switches and no problems were found.  No other alarms occurred this week.  A back flush air line separated from the north orifice in slot 6B on April 21, causing a slight intermittent water leak.  Since the associated turbine unit was out of service, the leak was not deemed an urgent matter and repairs were completed the next day.  Fisheries staff continues to monitor the collection channel during all shifts when primary bypass operations are taking place.  

Transportation Facility:  Spring bypass season continued with alternating days of primary and secondary bypass.  All sampled fish were returned to the river.  PIT tag detection occurs in the full flow pipe during primary bypass mode and throughout the facility during secondary bypass operations.  Smolt monitoring occurs only during secondary bypass days.  Primary (A and B) PIT tag slide gates remained off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The PIT tag system underwent scheduled maintenance this week without incident.  Sample gates continued to function well.  Ice block checks of the return to river lines removed one blockage in the A-side line and two blockages from the B-side line this week.  Otherwise, no problems observed during this report period.          

Transport Summary:  No fish transport is taking place at this time.  

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  The spring spill program continues with 40 percent of the river discharge being spilled.  Because of low river flows, spill patterns were adjusted for brief periods to allow towboats and barges safe entrance into and egression out of the navigation lock.       

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	149.1
	94.6
	60.0
	37.9
	51.6
	48.7
	5.5
	     4.8


*Control room data.  

Other

Inline Cooling Water Strainers:  The next approximate strainer cleaning date will be May 12.

Invasive Species: The zebra mussel detection stations were last inspected April 5, none were found.  The next examination of the zebra mussel stations will be approximately May 5. 

Predatory bird counts continued with tailwater and forebay observations conducted twice and once daily, respectively.  The tailwater high counts included eight gulls with an occasional cormorant or pelican being noted.  Most tailwater birds were seen in the spill area.  Only one gull was seen passing near the bypass outfalls.  Forebay area high counts included 40 grebes with an occasional gull or osprey being noted.  The water cannon continued to operate well.  APHIS bird hazing personnel are on duty seven days a week.  
Preparations for research studies continued.   The orifice lighting passage study group is making good progress.  On April 21, COE personal assisted researchers examining the release line outlet in turbine unit 6.  No problems were found.  
GBT monitoring continued.  

Project:  Ice Harbor

Biologist:  Mark Plummer 

Dates:  April 16 - 22, 2010

Turbine Operation
All turbine units (1 - 6) were available for operation this reporting period.  No problems to report.    

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways April 16, 19, 20, 21, and 22. 
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria 

Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.4 feet, off sill with a depth of 7.6 feet, off sill with a depth of 7.6 feet, off sill with a depth of 7.4 feet, and off sill with a depth of 7.5 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 8.0 feet, on sill with a depth of 8.7 feet, on sill with a depth of 8.7 feet, off sill with 9.5 feet, and off sill with 9.7 feet. The north shore entrance (NSE) was on sill with a depth of 6.0 feet, on sill with a depth of 6.0 feet, on sill with a depth of 6.0 feet, on sill with 6.7 feet, and off sill with 7.7 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria, except at the NSE.  The north fishway channel/tailwater differential varied from 1.5 feet to 2.5 feet this week.  The NSE was on sill and could not be lowered to reduce the head differential.  Channel/tailwater differential criteria are 1 – 2 feet.  During the April 16 inspection, the south channel/tailwater differential was at 2.2 feet.  Spill is making visual staff gage reading difficult due to rapid changes in water elevation at the staff gage.  Computer readings taken from the control point stilling wells indicate the fishways are in criteria at all points.  A trouble report has been initiated to confirm the fishway calibration.
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without any problems.  All north shore fish pump are in service.  Six south fish pumps were operated and 8 of the 8 south fish pumps are now in service.  South fish pump 4 returned to service April 21 at 1634 hours.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  

STSs/VBSs:  The STSs are in cycle run timing mode.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.  
Juvenile Bypass Facility:  The bypass was placed into operation March 8.

Juvenile Fish Sampling:  Sampling takes place on Mondays and Thursdays.  Due to the small number of fish being seen at Lower Monumental Dam, some sample days are being skipped. 

Removable Spillway Weir:  The RSW is in operation.

Fish Sampling:  
April 19:  No sample performed.

April 22:

	Species
	Sampled
	#Descaled
	Morts
	Avian Marks

	
	
	
	
	 

	C-CH
	9
	0
	0
	0

	UC-CH
	10
	0
	0
	0

	C-CH-O
	---
	---
	---
	---

	UC-CH-O
	---
	---
	---
	---

	C-SH
	4
	0
	0
	0

	UC-SH
	---
	---
	---
	---

	C-COHO
	---
	---
	---
	---

	UC-COHO
	---
	---
	---
	---

	C-SOCK
	---
	---
	---
	---

	UC-SOCK
	---
	---
	---
	---

	
	 
	 
	 
	 

	TOTAL
	23
	0
	0
	0


River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	61.1
	32.6
	47.5
	22.9
	47
	50
	5.8
	5.6


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Turbine unit cooling water strainers inspections were last completed April 2.  No lampreys were found.

Invasive Species: No zebra mussels were observed when the inspection was performed April 19. 
Spill for fish passage began April 3.  
Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Elizabeth Lindsey 

Dates:  April 16 - 22, 2010

Turbine Operation

All turbine units operated within the hard 1% operational constraint criteria.  There were no turbine unit outages during this week.   
Adult Fish Passage Facility

The adult fishway was inspected by Corps or WDFW biologists on April 16, 17, 18, and 21. 

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  Weir gate depth readings measured 6.6 ‘, 5.5’, 5.3’, and 5.0 feet while on sill.  South powerhouse channel/tailwater head differentials were in criteria (1’-2’) this week.    

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  Weir gate depth readings were 7.2’, 6.0’, and two at 5.8 feet while on sill.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head differentials were in criteria (1’-2’) this week.

Auxiliary Water Supply System: AWS pump 3 remains out of service for bearing housing replacement and diffuser assembly repair.  This work is scheduled to be completed in 2010.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.   
Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 0.8 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-30% surface coverage.  No oil was observed in gatewells.
STSs/VBSs:  STSs are operating in cycle mode.      

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass is in service with 19 orifices open. 
Collection Facility:  The facility is watered up and ready for collection and transport.  The collection of fish for condition monitoring began on April 1.  Subsequent collection for condition monitoring is taking place every third day from 0400 to 1200 hours. 
Transport Summary:  The facility is not collecting fish for transport at this time.  

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature (oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	60.3
	32.0
	24.3
	16.9
	50.0
	48.5
	4.8
	4.1


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers:  Turbine unit cooling water strainers were last cleaned on April 12.  Three lamprey mortalities were recovered.  
Invasive Species: There were no zebra mussels observed at the monitoring stations on the April 11 inspection.

Spring spill operation was initiated at 0001 hours on April 3.

Project:  Little Goose

Biologist: Richard Weis
Dates:  April 16 - 22, 2010

Turbine Operation

Turbine units 1 through 6 were available for service this report period.  All turbine units were operated within 1% of best efficiency. 
Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway April 16, 19 and 22.
Fish Ladder:  The ladder exit head differentials measured between 0.0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs was 1.1 feet (criteria 1.0-1.3 ft.) on all three inspections and picketed lead head differentials held steady at 0.0 feet (criteria < 0.3 ft.).  

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.14 and 1.70 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.18 and 8.32 feet (criteria ≥8.0 ft), NPE weirs rested on sill position and depths ranged between 5.44 and 5.86 feet (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 and depths measured between 8.46 and 8.60 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.12 and 6.24 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.5 and 2.3 fps near the SSE and 2.5 to 3.1 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 0.7 and 1.2 fps.  

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris inside the trash-sheer boom ranged from 15 to 50 square feet.     

Spillway Weir:  The weir is positioned in the high crest configuration (622 ft.) spilling approximately 7,200 cfs. 
ESBS/VBS:  All operating ESBSs were within criteria this report period.  The ESBS cleaning brush motor in slot 2B tripped a circuit breaker on April 19.  Normal operation resumed after the circuit breaker was reset.  Drawdown differentials for turbine units 1, 2 and 3 were measured on April 22.  All criteria were met.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection channel is operating satisfactorily with 21 open orifices.  
Transportation Facility:  The juvenile fish collection and transportation facility was switched from primary bypass to secondary bypass mode on April 21 at 0700 hours in support of collection for fish condition sampling.  Sample rates were set at 100%.  A total of 424 smolts were collected.  All fish were determined to be in good condition. Following an 8 hour sample period, the facility was placed back into primary by-pass at 1600 hours.

Transport Summary:  Fish collection for transport is scheduled to start May 1. 
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	61.9
	32.0
	18.8
	9.6
	52.9
	49.1
	5.8
	5.2


*Ladder temperature.

Other

Invasive Species:  The Zebra Mussel substrate monitor was last inspected on March 24, no mussels were observed.  The next inspection for zebra mussels is scheduled for April 23.  

Cooling Water Strainers:  Cooling water strainers were inspected on April 21.  No fish were found.

Avian Activity:  USDA – APHIS commenced piscivorous bird hazing on April 16.  Up to 9 gulls and 10 Cormorants were observed during a given day during this report period.

Project:  Lower Granite

Biologist: Mike Halter and Ches Brooks
Dates:  April 16 - 22, 2010

Turbine Operation

Lower Granite had turbine units 1, 2, 4, 5, and 6 available for power generation at the beginning of the report week.   Turbine unit 1 was taken out of service on April 20 when oil was found on the brush rigging and slip ring with mounds of carbon dust by the brushes.  The estimated return to service date is April 30.  Turbine unit 3 remained out of service for a rewind and will not be available until approximately December 31, 2010.
Adult Fish Passage Facility

On April 16, 17, and 19 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system. 
Fish Ladder:  All criteria were met.
Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were on sill during the first two inspections due to tailwater elevations below 633.0 feet.  During the April 19 inspection, tailwater elevations were just above 633.0 feet and both weirs should have had depths of just over 8 feet.  Gate 1 was slightly below criteria with a reading of 7.9 feet (criterion ≥ 1.0 feet).  Gate 2 met criteria with a reading of 8.0 feet.  North powerhouse fishway entrance weirs were on sill all week due to tailwater elevations below 636.0 feet.  Weir depths at the north powerhouse entrances ranged from 4.5 to 5.2 feet.  Weir depths at the north shore fishway entrances were out of critieria all week with readings between 5.1 and 5.2 feet on both gates (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.96 to 1.09 feet per second and averaged 1.01 feet per second.

Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated throughout the week without any problems.
Juvenile Fish Passage Facility

Juvenile fish numbers increased rapidly during the week and sample rates were dropped accordingly.  The sample rate was reduced from 20% to at 10% at 2000 hours on April 18.  At 0700 hours on April 19 the sample rate was lowered to 4%.   At 0700 hours on April 20 it was again lowered to 2%.  At 0700 hours on April 22 sample rates were reduced a third time, down to 1%.    

Forebay Debris/Gatewell Debris/Oil:  Debris accumulation in the forebay and gatewells was minimal.   It was not necessary to hand-dip debris from any gatewells this week.  
ESBSs/VBSs:   There were no problems with fish screens during the report week.  ESBS/VBS video inspections took place on April 23-25.  The only aberration found was 6 missing rivets from an ESBS retaining strap 47 feet down on the north side of gatewell slot 6A. 
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Orifices are being backflushed every three hours around the clock to ensure they remain free of obstructions that might impede fish passage.
Transportation Facility:  General transport operations are uncertain at this time but could start earlier than recent years due to the low flow forecast.  The first research barge departed Lower Granite on April 22.   The first regular barge trip is scheduled to leave on April 24.
Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	62.6
	33.2
	20.5
	20.2
	53.4
	51.8
	4.6
	4.0


*Scrollcase temperature.

Other
Inline Cooling Water Strainers:  The last inspection of the inline cooling water strainers took place on April 15.  The next inspection is scheduled for mid-May.
Invasive Species:   The zebra mussel monitoring station in the adult fishway exit was examined during the April 12 fishway inspection.  No evidence of zebra mussels was found.

Research:  The University of Idaho continued steelhead kelt research work at the recently constructed holding tanks upstream of the main fish facility.  Clipped and unclipped kelts are being examined and returned to the tailrace.  Blood samples are also being also being taken from a few unclipped steelhead kelts. 

NOAA-Fisheries tagged fish for the survival study and barge index study on April 20, 21 and 22.
The sample rate at the adult fish trap was reduced from 15% down to 4% at 1430 hours on April 18.  Wild steelhead are being PIT-tagged and genetic and scale samples are being taken.  In addition, scale samples are being taken from one out of every 25 hatchery steelhead .  One out of every seven hatchery Chinook are also being PIT-tagged and scale samples and genetic materials are being taken.  Two sort-by-code projects are also under way:  1) up to 15 Lemhi-origin chinook are to be diverted for radio-tagging,   2) Chinook that were acoustic-tagged in the estuary are being diverted to check the recovery status of the surgery and take reference photos.

