
U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#11-2010
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  May 7 - 13, 2010
Turbine Operation

McNary had 14 turbine units available for power generation this week.  On May 10, turbine unit 1 was out of service for two hours for VBS replacement in slot 1C.  On May 13, turbine units 5 and 14 were out of service a total of two hours in support of ESBS video-camera inspections.  
Except for turbine units 4 and 5, all available turbine units operated within the hard 1% efficiency criteria this week.  Turbine units 4 and 5 operated outside 1% criteria in support of research.  The study protocol requires one turbine unit to be operated at 70 MW, while the other turbine unit operates at the upper end of 1% peak efficiency.  These turbine units are alternately operated in this manner from Monday through Friday with the switch occurring at 1200 hours each day.         

Adult Fish Passage Facilities

On May 8, 10 and 13, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts continued.  On May 10, diffuser valves in the Oregon ladder underwent maintenance.      

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections except on May 8 when the Washington ladder count station differential measured 0.7 feet.    Operators resolved the problem by cleaning the picketed leads.  The next day, fisheries staff removed tumble weeds from the leads along with two smolt mortalities.  A regulating weir and low water alarms respectively sounded near the Washington ladder exit on May 8 and 9.  In both cases, normal operation resumed after the alarm was reset.  At the Oregon exit, weir 338 also triggered an alarm this once week.  Normal operation was restored after the alarm was reset.  Both Oregon exit traveling screens have been operating well and differential monitoring has revealed no problems.  Picketed leads in both ladders are being closely monitored daily due to the amount of floating debris in the river.                    

Fishway Entrances and Collection Channel:  Both ladders met all inspection points criteria except on May 8 when Washington entrance W3 measured a 7.8 feet differential.  Entrance weir W2 also triggered an alarm that day.  Normal operation resumed after the alarm was reset.  These two entrance weirs appear to be the ones most affected by hydraulic gradients produced by the spill and low tailwater elevations.  Collection channel velocity averaged 1.5 feet per second.    

Auxiliary Water Supply System:  All three fish pumps operated satisfactorily with blade angles of approximately 24 degrees.  The juvenile facility continues to add 450 cfs to the north powerhouse pool except for approximately a seven hour outage described in the juvenile fish passage section below.  The Wasco County PUD turbine unit no interruptions in service during this report period.

Juvenile Fish Passage Facility

Alternate days of primary and secondary bypass operations continued, with the switch between bypass modes occurring each morning at 0700 hours.  Deviations from this schedule took place on three occasions this week.  The first took place from 1900 to 2306 hours on May 9, in support of the orifice lighting study.  During this time, sample rates were set at 10% which resulted in the collection of 2,259 smolts for research purposes.  See below for details for the second and third deviations from the schedule.  For this report period, 401,780 smolts were routed to the tailrace during routine secondary bypass operations.  

On May 11 (a primary bypass day), fish were evacuated from the facility in support of planned dewatering of the collection channel.  This operation would have permitted rectangular dewatering screen cleaner repairs.  However, service unit 1 which supplies the emergency supply water under these kinds of circumstances had not yet been returned to service.  Since study fish were still being held at the facility, the channel dewatering was delayed until the next day.  Planned sampling for research purposes on May 11 was postponed to insure no fish would be in the facility when the channel was be dewatered.  Research fish were collected with the regularly sampled fish on May 12.  On May 12, at 0500, the last group of study fish were removed from the facility and released at 6B gatewell slot with the orifice trap open.  The facility remained in primary bypass as the collection channel while orifices were closed from 0740 – 0900 hours.  During this period, the service unit (mentioned above) returned to service making flush water and full flume flow available during the collection channel dewatering operation.  No emergency water was needed at the collection and transport facility as no fish were present.  Collection channel water levels were lowered far enough to provide safe work conditions.  Fish evacuations were not necessary as the remaining water in the channel provided sufficient sanctuary.  Repairs to the cleaner retracting cables were completed by 1330 hrs.  Normal collection channel and orifice operations were restored by 1515 hours, followed by the start of previously scheduled secondary bypass (and sampling) at the fish facility at 1521 hours.  During the outage, the gatewell slots and the collection channel were closely monitored and no problems were observed.  Approximately 12 juvenile lampreys were removed from the separator and returned to the river during this outage.  
Primary bypass became necessary from 658 to 1800 hours on May 12 following a ten minute power outage in the collection channel.  The outage was caused by a power surge following line switching in the powerhouse.  Primary bypass operations reduce complications from collection channel water fluctuations that typically follow power outages.  During this time, the sample gates remained active and a biologist was monitored the channel as the side dewatering valves repositioned themselves after the power outage.  No other interruptions in facility operations occurred this week.        

Forebay Debris/Gate well Debris/Oil:  Forebay debris remains light with flows and wind dispersing incoming floating debris which includes tumbleweeds.  Some debris is being drawn towards turbine units 4 and 5 when they operate at higher electrical loads.   Trash rack differentials have revealed no problems and no racks were cleaned this week.  No problems were observed in the gatewell slots including those associated with turbine units 4 and 5.  Turbine units 4 and 5 were also operated at higher electrical loads during the collection channel outage mentioned above.  

ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  At the beginning of the report period, the screens in slots 5C, 6A and 7C were in transducer bypass mode.  ESBS in slots 6A and 7C were returned to automatic mode on May 13 following electrical cable repairs.  The screen in slot 14A was serviced 3 times this week, beginning with an alarm on May 8.  Normal operation resumed after the alarm was reset.  On May 10, the screen exhibited short operating cycles.  A video camera inspection on May 13 revealed wood underneath one of the cleaning brush drive chains.  The brush was cycled several times to flatten and dislodge the wood.  No problems were observed after maintenance personnel reset and adjusted the brush operating parameters (software).  ESBS video-inspections were conducted in turbine unit 5 on May 13, and no problems were found.  VBS differential monitoring efforts revealed no unusual readings this week and no cleaning operations were necessary.  The VBS in slot 1C was replaced with rehabilitated screens on May 10 as part of a program to eventually replace the mesh on all 42 screens. 

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, 42 orifices were in use.  As mentioned above, the collection channel was taken out of service for 7 hours in support of screen cleaner repairs on May 12. At times, extra orifices were opened in slots 4A and 5A by the NOAA researcher to assist in fish evacuation prior to gatewell dipping.  These extra orifices were swapped with those in a non-operating unit for a short period, usually less than two hours in order to maintain the 42 orifice count.

An orifice obstruction was found on May 13 after NMFS researchers had trouble using their gatewell dipping trap in slot 5A.  Corps personnel observed unusual flow patterns and unsuccessfully backflushed orifice 5A north several times.  A subsequent video inspection revealed a large stick across the gatewell face of the orifice.  Gatewell dipping and normal orifice operations resumed after the stick was removed.     

On May 14, an orifice in slot 7A was left closed and an extra orifice in slot 6B slot was found opened.  Since turbine unit 7 had been operating intermittently with closed orifices in slot 7B for only a couple hours, few if any fish were likely in the gatewells.  Although the cause of this operating condition was never determined, both researchers and facility staff reviewed procedures for swapping orifices.  Researchers no longer plan to swap orifices as gatewell dipping should adequately remove the fish from the slots.  No other problems were observed in the collection channel this week and all systems operated well in automatic mode.  Fisheries personnel continue to monitor the collection channel during all shifts when primary bypass operations are taking place.  Fisheries personnel are also monitoring all three orifice traps associated with the orifice lighting study.   

Transportation Facility:  Spring bypass season continued with alternating days of primary and secondary bypass.  All sampled fish were returned to the river.  PIT tag detection occurs in the full flow pipe during primary bypass mode and throughout the facility during secondary bypass operations.  Sampling and smolt monitoring occurs only during secondary bypass operations.  Limited sampling and secondary bypass operations are taking place on scheduled primary bypass days in support of the NMFS orifice lighting study.   When extra sampling occurs on primary bypass days, Corps data only includes adult fallback counts.  Primary (A and B) PIT tag slide gates remained off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The PIT tag system underwent scheduled maintenance this week without incident.  Sample gates continued to function well.  Ice block checks of the return to river lines indicated no blockages.  Maintenance activities include operations in support of dewaterer repairs on May 12 (see above) and the installation of a new GBT water supply pump foot valve on May 11. 

Transport Summary:  There is nothing to report. 

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours each day.  The spring spill program continues with 40 percent of the river discharge being spilled.  Because of low river flows, spill patterns were adjusted for brief periods to allow towboats and barges safe entrance into and egression out of the navigation lock. 

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	188.5
	163.0
	76.0
	65.4
	51.9
	50.5
	6.0
	     5.0


*Control room data.  

Other

Inline Cooling Water Strainers:  Cooling water strainer cleanings are scheduled later this month.

Invasive Species: No invasive species were found during the May 1 detector inspection.  The next inspection is approximately scheduled for June 1.  

Predatory bird counts continued with tailwater and forebay observations conducted twice and once daily, respectively.  The tailwater high counts included 215 gulls and 12 pelicans.  Most tailwater birds were seen in the spill area after hours when hazing personnel are not present.  High counts at the bypass outfalls included 3 gulls and 4 pelicans.  Forebay area high counts included 136 grebes, 4 pelicans with an occasional gull, cormorant or osprey being noted.  Pelicans are also roosting on the rocks by the Washington side boat ramp.  Four grebes entered the gatewell slots, joining a grebe noted the previous week.  One of the 5 grebes entered the collection channel and passed out of the system unobserved, leaving four grebes in the slots.  The water cannon continued to operate well.  APHIS bird hazing personnel are on duty seven days a week.  

The orifice lighting and one percent criteria studies continued as did GBT monitoring efforts.  

Project:  Ice Harbor

Biologist:  Mark Plummer 

Dates:  May 7 - 13, 2010

Turbine Operation
All turbine units (1 - 6) were available for operation during this reporting period.  Turbine units 4 through 6 were out of service May 12 for short periods while STS and cooling water strainers were inspected.
Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways on May 7, 10, 11, and 13. 
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria 

Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 9.5 feet, off sill with a depth of 8.8 feet, off sill with a depth of 8.6 feet, and on sill with a depth of 8.8 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 7.4 feet, off sill with a depth of 7.7 feet, on sill with a depth of 9.2 feet, and on sill with 8.9 feet. The north shore entrance (NSE) was on sill with a depth of 7.1 feet, off sill with a depth of 7.9 feet, off sill with a depth of 8.3 feet, and on sill with a depth of 6.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  On May 7 and 10 the north powerhouse entrance (NFE) was out of criteria.  Criteria were met after the operator was notified and adjusted the fishway controls.  All channel/tailwater differentials were in criteria.  Spill is making visual staff gage reading difficult due to rapid fluctuations in water elevation at the staff gages.  
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  All north shore fish pump are in service.   Six of the 8 available south fish pumps were operated.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactory.  

STSs/VBSs:  STSs are operating in cycle run timing mode.  No problems were found in the during the May STS/VBS inspections.  
Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.  
Juvenile Bypass Facility:  The bypass was placed in operation March 8.

Juvenile Fish Sampling:  Sampling for fish condition takes place on Monday and Thursday.  

Removable Spillway Weir:  The RSW is in operation.

Fish Sampling:  
May 10:  

	Species
	Sampled
	#Descaled
	Morts
	Avian Marks

	
	
	
	
	 

	C-CH
	20
	1
	0
	0

	UC-CH
	5
	0
	0
	0

	C-CH-O
	---
	---
	---
	---

	UC-CH-O
	---
	---
	---
	---

	C-SH
	131
	3
	0
	2

	UC-SH
	13
	0
	0
	0

	C-COHO
	---
	---
	---
	---

	UC-COHO
	---
	---
	---
	---

	C-SOCK
	---
	---
	---
	---

	UC-SOCK
	---
	---
	---
	---

	
	 
	 
	 
	 

	TOTAL
	169
	4
	0
	2


May 13:

	Species
	Sampled
	#Descaled
	Morts
	Avian Marks

	
	
	
	
	 

	C-CH
	12
	0
	0
	0

	UC-CH
	2
	0
	0
	0

	C-CH-O
	---
	---
	---
	---

	UC-CH-O
	---
	---
	---
	---

	C-SH
	110
	1
	0
	0

	UC-SH
	12
	0
	0
	0

	C-COHO
	---
	---
	---
	---

	UC-COHO
	---
	---
	---
	---

	C-SOCK
	---
	---
	---
	---

	UC-SOCK
	---
	---
	---
	---

	
	 
	 
	 
	 

	TOTAL
	136
	1
	0
	0


River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	54.7
	45.2
	41.8
	13.5
	53
	53
	4.2
	4.0


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Thirty-one juvenile lamprey mortalities were removed from cooling water strainers on May 12.  Of these, 15 of these were found in turbine unit 4, eight were found in turbine unit 5 and 8 were removed from turbine unit 6.  Other mortalities recovered included 2 unidentified fish (one each in turbine units 4 and 5) and one juvenile clipped steelhead in turbine unit 4. 
Invasive Species: No zebra mussels were observed during inspections on May 7, 10 and 11. 
On May 11, a fish salvage operation was conducted the vicinity of the navigation lock tainter valve at the north end of the dam.  Approximately 60 steelhead smolts and 60 Chinook smolts were recovered and released into the forebay.   

Spill for fish passage began April 3.  

Project:  Lower Monumental Dam

Biologists:  Bill Spurgeon and Elizabeth Lindsey 

Dates:  May 7 - 13, 2010

Turbine Operation

All turbine units are being operated within soft constraint of the 1% operation criteria.  There were no turbine unit outages during this week.   
Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on May 7, 8, 9, and 12. 

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 6.0’, 5.9’, 5.5’, and 5.4 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) this week.    

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 6.6’, 5.6’, 5.4’, and 5.5 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Auxiliary Water Supply System: AWS pump 3 remains out of service for bearing housing replacement and diffuser assembly repair.  This work is scheduled to be completed in 2010.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.   

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 1.0 square yard of forebay debris observed during this period.  Gatewell debris ranged from 0-25% surface coverage.  No oil was observed in gatewells.
STSs/VBSs:  STSs are operating in cycle mode.      

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is watered up with 19 orifices open.  
Collection Facility:  Collection of fish into raceways for transport began at 0001 hours on May 4.
Transport Summary:  Every-day barging began on May 5.  

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	51.8
	45.4
	37.2
	30.2
	51.5
	50.0
	3.9
	3.5


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers:  Turbine unit cooling water strainers were cleaned May 12.  See table 2 below for details.  
Table 2. May 12, 2010  turbine unit cooling water strainer inspection results. 

	
	Lamprey
	Salmon
	Steelhead
	Siberian Prawn

	Unit
	Live
	Dead
	Live
	Dead 
	Live
	Dead
	

	1
	0
	2
	0
	0
	0
	0
	1

	2
	0
	22
	0
	0
	0
	0
	3

	3
	0
	0
	0
	0
	0
	0
	0

	4
	0
	0
	0
	0
	0
	0
	0

	5
	0
	10
	0
	1
	0
	1
	2

	6
	0
	0
	0
	0
	0
	0
	0


Invasive Species: There were no zebra mussels observed at the monitoring stations during the May 7 inspection.

Spring spill operation was initiated at 0001 hours on April 3.

Project:  Little Goose

Biologists: Richard Weis
Dates:  May 7 - 13, 2010

Turbine Operation

All turbine units were available for service during this reporting period.  All turbine units were operated within 1% of best efficiency. 
Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway May 7, 10 and 12.
Fish Ladder:  The ladder exit head differentials remained constant at 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs was 1.1 feet (criteria 1.0-1.3 ft.) for all three inspections and picketed lead head differentials held steady a 0.0 feet (criteria < 0.3 ft.).  

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials at all fish entrances ranged between 1.24 and 2.08 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.02 and 8.32 feet (criteria ≥8.0 ft), NPE1 and 2 wears rested on sill position and depths ranged between 5.02 and 5.48 feet (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 feet and depths measured between 7.70 and 8.34 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.10 and 6.16 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.3 and 2.3 fps near the SSE and 2.7 to 3.2 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 0.7 and 1.0 fps.  

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris inside the trash-sheer boom ranged from 0 to 20 square feet.   Gatewells remained clear of debris and oil.  Trash rack raking scheduled for May 11 and 12 did not occur as the rake is removed from service requiring cable repairs.  All indications (fish condition, drawdown measurements) favor minimal debris loading on the trash racks.   

Spillway Weir:  The weir was positioned in the high crest (622 ft.) mode, spilling approximately 7,200 cfs until May 13, when it was reconfigured to low crest  mode, spilling approximately 11,300 cfs. 
ESBS/VBS:   All operating ESBS were within criteria this report period.  Drawdown measurements across trash racks, ESBS and VBS associated with turbine units 1 and 2 were performed on May 13, all criteria were met.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection channel is operating with 21 open orifices.  
Transportation Facility:  Collection and transport operations continued. Daily collection for the period ranged between 22,750 and 37,050 totaling 190,152 for the week.  All fish were transported except for mortalities.  Descaling and mortality rates for this report period are 0.3% and < 0.1% respectively.  
Transport Summary:  Collection and transport continued this report period.  All barge loading operations were successfully performed.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	51.0
	46.3
	15.4
	13.8
	51.6
	49.5
	5.5
	4.8


*Ladder temperature.

Other

Invasive Species:  The Zebra Mussel substrate monitor was inspected on April 30, no mussels were observed.  The next inspection for zebra mussels is scheduled for May 23.  

Cooling Water Strainers:  Cooling water strainers were inspected on May 12. 

Avian Activity:  USDA – APHIS continued piscivorous bird hazing operations.  Up to 300 gulls and 15 Cormorants were observed during a given day this report period.

Project:  Lower Granite

Biologist: Mike Halter and Ches Brooks
Dates:  May 7 - 13, 2010

Turbine Operation

Lower Granite had turbine units 1, 2, 4, 5, and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remained out of service for a rewind and will not be available until approximately December 31, 2010.
Adult Fish Passage Facility

On May 7, 8, 11, and 13 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system. 
Fish Ladder:  All criteria were met with the exception of the ladder weir depth at diffuser 14 which was 0.9 feet (0.1 feet below criteria) on the May 11 inspection (criterion 1.0 – 1.3 feet).
Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were on sill during the May 7 and May 8 inspections with respective depths of 7.8 and 7.9 feet on both gates.  Tailwater elevations increased enough to bring the gates off their sills on the May 11 and May 13 inspections and both gates met the 8.0 foot criteria level.  North powerhouse fishway entrance weirs were on sill all week due to tailwater elevations below 636.0 feet.  Weir depths at the north powerhouse entrances ranged from 5.1 to 5.3 feet.  Weir depths at the north shore fishway entrances were out of critieria all week with readings of between 4.9 and 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.90 to 1.02 feet per second and averaged 0.96 feet per second.

Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.  The three 4160 backup fish pumps at the head of the fish ladder were operationally checked on the afternoon of May 11.   All operated properly.
Juvenile Fish Passage Facility

The sample rate was increased from 0.5% to 1.0% at 0700 hours on May 7.  The sample rate remained at 1% until 0700 hours on May 10 when it was increase to 2% to help accommodate fish marking needs in the lab.  The sample rate was reduced back down to 1% at 0700 hours on May 11 and remained at that level through the remainder of the report week.    

Forebay Debris/Gatewell Debris/Oil:  Debris accumulation in the forebay and gatewells was minimal.  It was not necessary to hand-dip debris from any gatewells this week.  
ESBSs/VBSs:  There were no problems with fish screens during the report week.  The next ESBS/VBS inspections are scheduled for May 21-23.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Orifices are being backflushed every three hours around the clock to ensure they remain free of materials that might impact fish passage.
Transportation Facility:  All aspects of facility operation at Lower Granite have been going smoothly.
Transport Summary:  Every day fish barging operations continued at Lower Granite, Little Goose, and Lower Monumental Dams.  All aspects of the operation have been going smoothly.  
Removable Spillway Weir:   Nothing unusual to report on the RSW. 
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	52.5
	47.6
	20.6
	20.4
	52.4
	50.9
	4.8
	3.1


*Scrollcase temperature.

Other
Invasive Species:   The zebra mussel trap at the adult fishway exit was last examined for zebra mussels on May 11.  No evidence of zebra mussels was found.

Lamprey:  The last inspection of the inline cooling water strainers took place on April 15.  The next inspection is scheduled for next week.
Research:  The University of Idaho continued steelhead kelt research work at the recently constructed holding tanks upstream of the main fish facility.   Steelhead kelts are being examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts were blood sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river during the report week.   Steelhead kelts are now being barged on Wednesdays.

NOAA-Fisheries personnel tagged fish for the survival study, extra mortality study, and transport study at the JFF trailers during the week.  Smolts from the transport study and roughly half from the extra mortality study were barged to below Bonneville.

PNNL personnel continued marking fish for the Survival and Behavior Study through the Columbia River Estuary with acoustic tags.   This study will examine the migratory behavior and ocean-entry timing of both stream and ocean type juvenile Chinook through the lower Columbia River and the Columbia River estuary and plume.  

Idaho Department of Fish and Game personnel conducted genetic stock identification work on Chinook and steelhead smolts from the lab during the week.  The goal of the study is to enumerate and characterize the natural production of spring/summer Chinook salmon and steelhead above Lower Granite with regard to age composition and genetic stock identification.  Sampling is taking place every day with a goal of collecting between 2500 and 4000 genetic samples from both Chinook and steelhead. 

The adult fish trap operated at a 4% sample rate during the week.  Wild steelhead are being PIT-tagged and genetic and scale samples are being taken.  In addition, scale samples are being taken from one out of every 25 hatchery steelhead .  One out of every seven hatchery Chinook are also being PIT-tagged and scale samples and genetic materials are being taken.  Two sort-by-code projects are also under way:  1) up to 15 Lemhi-origin Chinook are to be diverted for radio-tagging,   2) Chinook that were acoustic-tagged in the estuary are being diverted to check the recovery status of the surgery and take reference photos.

