U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#23-2010
Project:  McNary

Biologists:  Brad Eby and Bobby Johnson

Dates:  July 30 – August 5, 2010
Turbine Operation

McNary had eight to ten turbine units available for power generation this week.  Turbine  units 2 and 7 are expected to remain out of service for a rewind contract until the end of the year.  Turbine units 3 and 4 remain out of service in support of T2 transformer, replacement.  Transformer replacement is expected to be completed in approximately three weeks.  On August 1, turbine units 10 and 11 were out of service a total of 46 minutes for ESBS video-camera inspections.  From August 2 to 5, turbine unit 5 was out of service for annual maintenance and VBS replacement in slot 5B.  On August 4, turbine unit 11 was taken out of service for ten hours to allow repacking of the governor hydraulic oil head cover.  
Individual turbine units underwent validation tests this week.  Validation tests determine actual generator component operating parameters.  Model validation is required by industry enforced standards to ensure predicted electrical system reliability.  From August 2 to 3, turbine unit 1 was out of service for validation testing and VBS replacement in slot 1B.  Additional tests took place August 3 to 4 in turbine unit 6, August 4 in turbine units 8 and 9 (six hours total outage time), August 4 to 5 in turbine unit 10, August 5 in turbine unit 11 (3.3 hours outage time) and August 5 to 6 (turbine unit 13).

On August 3, north powerhouse loading was recommended by the project personnel to moderate juvenile fish collection channel temperatures after the T2 transmission line returns to service.  Although current turbine operations are limited by the transmission line outage, the current configuration is sufficient to maintain reasonable temperatures within the collection channel.  No turbine units operated outside 1% peak efficiency criteria this week.

Adult Fish Passage Facilities

McNary fishery biologists performed measured inspections of the adult fishways on July 30, August 1 and 3.  Adult fish counting season continues.  Oregon entrance weirs SFEW1, SFEW2 and NFEW1 are being lowered during nighttime hours on a predetermined schedule as part of the adult lamprey passage study.  No problems have been observed.  Ladder exit temperature monitoring continues.      

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  A regulating weir in the Washington ladder triggered alarms on 5 occasions.  In each case, normal operation resumed after the alrm was reset.  The Oregon ladder exit also triggered an alarm on Sunday, August 1.  Closer inspection revealed Eurasian milfoil clogging the picketed leads resulting in approximately one foot of flow over the leads and the adjacent walkway.  The ladder flow level set point was reduced and a crew was able to respond about mid day to clean the leads.  An Ice Harbor crane operator also assisted with this work.  Changing winds had caused much of the forebay debris to shift location overnight and enter the fishway. Fish passage remained unaffected.  A couple of shad were trapped in a small corner enclosure and later recovered and released.  The August 1 fishway inspection results do not reflect this abnormality as the inspection was conducted after the incident was resolved.  The north Oregon exit traveling screen remains out of service. The south traveling screen continues to operate well and differential monitoring revealed no problems.                         

Fishway Entrances and Collection Channel:  At the Washington ladder, all inspection points were in criteria.  Readings at entrance weir W2 are being taken from a cable drum indicator as the digital display needs a new LED.  All Oregon ladder inspection points were also in criteria except for the north powerhouse pool differential which measured 0.5 to 0.9 feet.  Low tailwater elevations and hydraulic gradients continue to affect measurements.  Collection channel velocities averaged 1.4 feet per second.    

Auxiliary Water Supply System:  Fish pumps 2 and 3 ran satisfactorily this week with blade angles of 30 degrees and no interruptions in service.  Fish pump 1 remains out of service as only two pumps can be operated with transformer 2 being unavailable.  The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit no interruptions in service during this report period.

Juvenile Fish Passage Facility

Fish collection for barge transport continued.  On August 5 at 1000 hours following regional discussions, daily transport operations were initiated.  A barge departed the facility as previously scheduled on August 5, and a truck is scheduled to depart the facility on August 6.  Barge and trucks will continue to transport fish on alternate days until the start of every-other-day fish truck operations on August 18.  No other changes in facility operations occurred during this report period.  For the week, 55,910 smolts and 200 juvenile lamprey were collected.         

Forebay Debris/Gate well Debris/Oil:  Forebay debris was very light even though some debris remains in the area around the Oregon ladder exit.  Trash rack differentials revealed no problems and no racks were cleaned.  Slots 3B, 3C, 4A and 4B slots remain covered in support of the transformer 2 replacement contract.  No problems were observed in the gatewell slots.  

ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  Screens at in slots 5C, 6A, 9C and 10C remain in transducer bypass mode.  On August 1, ESBS and orifice camera inspections took place in turbine units 10 and 11 with satisfactory results.  Although VBS monitoring revealed no screens out of criteria, 8 screens were cleaned on July 30 as a preventative measure.  During these cleaning operations, a small tear was observed in slot 1B and the VBS was replaced August 3 as a preventative measure.  On August 2, VBS inspections and screen cleaning occurred at turbine units 5 through 7.  Tears were observed in the mesh on the screen in slot 5B which could potentially pose a fish passage problem.  The affected turbine unit was already out of service and the VBS was replaced on August 5.      

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Thirty-nine orifices were in use all through the week as forebay elevations remain stable.  The orifices associated with turbine units 2 or 3 (which are out of service) are opened or closed as required during when forebay elevations are high.  This permits side dewatering valves operation in a more favorable range.  All systems operated well in automatic mode.  Fish facility staff continued to monitor the collection channel during VBS cleaning activities.             

Transportation Facility:  Collection for transport continued with barge loading occurring every other day until August 5 at 1000 hours when daily transport was begun as described above.  Truck and barge transport operations are now taking place on alternate days.  

Primary (A and B) PIT tag slide gates are currently in service and PIT tagged fish are being routed directly to the river.  The secondary (C and D) PIT/bypass gates remain closed and off for fish collection.  Sample gates continued to function well.  Ice block checks of the barge loading lines indicated no blockages.  Raceways are being switched every 24 hours to reduce fish stress.  Fish mortality rates ranged from 0.23 to 3.35 percent for the week.  Preparation for truck transport operations continued.  On August 4, a successful test trip was taken to the release site near the Bonneville Smolt Monitoring Facility.  Fish transport by truck will commence August 6.               

Transport Summary:  Barges departed from the McNary facility on July 30, August 1, August 3 and August 5.  The August 5 barge contained fish collected from August 3 to 1000 hours on August 5.  Fish collected after 1000 hours were to be transported by truck the following day.  There are no problems to report this week.  

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours each day.  The summer spill program continues with 50 percent of the river discharge being spilled.  Spill patterns were adjusted for brief periods to allow towboats and barges safe entrance into and egression out of the navigation lock.  Operators did report some problems this week with the software program controlling the spill gates.  ODFW personnel began water temperature monitoring efforts on June 15.  Monitoring results are reported separately.  Water temperatures are being monitored closely and though there are concerns, no problems have been observed.
Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	158.1
	110.8
	78.8
	55.4
	71.5
	69.1
	6.0
	     6.0


*Control room data.  

Other

Inline Cooling Water Strainers:  Cooling water strainer cleanings are scheduled to take place later in August.  The last inspection took place on June 14.  
Invasive Species: No invasive species were found during the August 1 detector inspection.    
Predatory bird counts continued with tailwater and forebay observations conducted twice and once daily, respectively.  Bird numbers appeared to have decreased along with declining numbers of fish present.  The tailwater high counts included 18 gulls, 8 cormorants, 7 pelicans and 3 terns.  Most tailwater birds were seen in the spill area.  Pelicans tended to work the calmer edges of the spill area.  No birds were seen around the bypass outfalls.  Forebay area high counts included 22 grebes, 5 juvenile gulls, 4 pelicans with an occasional osprey being noted.  No addition grebes joined the single remaining grebe noted in the gatewell slots last week.  The 3 grebes noted in the collection channel last week are still present.  The water cannon continued to operate well.
The adult lamprey passage studies continued as did GBT monitoring efforts.  

Project:  Ice Harbor

Biological Technician: Stephen B. Jeffers 
Dates:  July 30 – August 5, 2010

Turbine Operation
Turbine units (1 – 4 and 6) were available for operation during this reporting period.  Turbine unit 5 went out of service July 19th at 0635 hours for annual maintenance.

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways on August 2, 3, 4, and 5. 
Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. 

Fishway Entrances and Collection Channel (inspection date order): The south shore entrance (SFE) was on sill with a depth of 6.9 feet, off sill with a depth of 7.7 feet, off sill with a depth of 7.9 feet, and off sill with a depth of 7.9 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.1 feet, on sill with a depth of 8.1 feet, on sill with 9.5 feet, and on sill with a depth of 8.0 feet. The north shore entrance (NSE) was on sill with a depth of 5.2 feet, on sill with a depth of 7.2 feet, on sill with a depth of 6.7 feet, and on sill with a depth of 6.9 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The north fish entrance and the north powerhouse fish entrance are being operated in manual mode due to spill causing constant weir adjustments and weirs jamming in their tracks.  All out of criteria depths were reported to the operator for corrections.  All channel/tailwater differentials were in criteria.  Spill continues to make visual staff gage reading difficult due to rapid changes in water elevation at the staff gages.  Visual staff gage readings are utilized in this report.  
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without any problems.  All north shore fish pumps are in service.  Seven of the 8 south shore fish pumps were available for service this week.  Of these, 6 were operated.  South fish pump 4 previously went out of service July 23 for repairs due to excessive noise from the motor bearings.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There is minimal forebay debris.  Fish ladder exits are clear of debris and the bubblers are operating.  

STSs/VBSs:  STSs are being operated in continuous mode.  STS/VBS inspections are currently slated scheduled for August 9th and 11th.
Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  Twenty orifices are open.  The collection channel screen cleaner went out of service August 2nd due to the cable malfunctioning.  The screen cleaner control switch has been placed in manual mode and being operated as needed until repairs can be made.   
Juvenile Bypass Facility:  The bypass was placed in operation March 8.

Juvenile Fish Sampling:  Sampling for the 2010 season concluded July 1 when the number of juvenile fish sampled during a 4 hour period dropped below 100 on 2 consecutive sample dates.  

Removable Spillway Weir:  The RSW is in operation.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	40.3
	35.2
	30.2
	25.3
	70
	69
	6.2
	6.2


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainer cleanings are scheduled to take place next week.  The last inspection took place July 14.  
Invasive Species: No invasive species were found during inspections on August 2 and 4.    
Project:  Lower Monumental Dam

Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates:  July 30 – August 5, 2010

Turbine Operation

All turbine units are being operated within the hard constraint 1% operational criteria.  Turbine units 1 through 6 were taken out of service from July 26 at 0553 hours to July 30 at 1915 hours in support of transformer doble tests.  During this period turbine unit 5 ran in speed-no-load mode for station service during the day (0600-1800 hours).  Turbine units 5 and 6 were available for generation nightly from 1800-0600 hours.  Turbine unit 2 was taken out of service for annual maintenance on August 2 at 0809 hours.  Turbine unit 4 was out of service on August 2 from 0804 to 1256 hours after a low oil relay tripped.  All turbine units were rotated out of service on August 2 and 3 during STS inspections.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on July 30, 31, and August 3 and 4. 

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections. North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 5.2’, 5.4’, 6.0’, and 6.7 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’).    

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 6.0’, 6.1’, 6.2’ and 7.0 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’).

Auxiliary Water Supply System: AWS pump 3 remains out of service to replace the bearing housing and repair the diffuser assembly.  This work is scheduled to be completed in 2010.  Pumps 1 and 2 were in service throughout this period.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.   

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 8.1 square yards of forebay debris observed during this period.  Gatewell debris surface coverage ranged from 0-15 percent.  No oil was observed in gatewells.
STSs/VBSs:  STS operation is in continuous run mode as the average fork length of sub-yearling chinook and/or sockeye is less than 120mm.  STS inspections were conducted on August 2 and 3.  All screens passed inspection. 
Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 19 opened orifices.  
Collection Facility:  No problems were observed in facility systems or operation. 
Transport Summary:  Every-other-day barging is in progress.  The last barge will be August 16 and first truck August 18.
River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	39.6
	35.1
	24.6
	15.1
	69.0
	68.0
	4.9
	3.6


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected August 2.  See Table 2 for results.

Table 2. Results Aug 2, 2010 cooling water strainer inspections at Lower Monumental Dam
	
	Lamprey
	Salmon
	Steelhead
	Siberian Prawn

	Unit
	Live
	Dead
	Live
	Dead 
	Live
	Dead
	

	1
	0
	0
	0
	0
	0
	0
	3

	2
	0
	0
	0
	0
	0
	0
	6

	3
	0
	0
	0
	0
	0
	0
	4

	4
	0
	1
	0
	0
	0
	0
	3

	5
	0
	1
	0
	0
	0
	1
	1

	6
	0
	0
	0
	0
	0
	0
	1


Invasive Species:  There were no zebra mussels observed at the South shore monitoring stations on July 11.  During this inspection, the North shore mussel trap was found to be missing.  A new trap was deployed on July 16. 

Summer spill operations was initiated at 0003 hours on June 21.  The average spill for this period was 17.8 kcfs.
The navigation lock was taken out of service from 0850 to 1345 hours on August 5 for lift gate gearbox inspection.
Project:  Little Goose

Biologist:  George Melanson
Dates:  July 30 – August 5, 2010

Turbine Operation

Turbine unit 6 was available for power generation through this reporting period.  Turbine unit 4 has been out of service for annual maintenance since July 27.  Turbine unit 5 was forced from service August 2 at 0615 hours to August 3 at 0829 hours due to transducer synchronization errors.  Turbine units 1 through 3 were removed from service on August 3 at 0958 hours through the remainder of this report period in support of power line maintenance, doble testing and transformer repairs.  There were no reports of turbine units operating outside 1% peak efficiency.

Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on July 30, August 2 and 5.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs was ranged between 1.0 and 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady a 0.0 feet (criteria < 0.3 ft.).   A 20 gallon plastic drum (debris) was removed from the ladder exit trash rack on August 5. 

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials at fish entrances ranged between 1.14 and 1.70 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.26 and 8.50 feet (criteria ≥8.0 ft), NPE1 and 2 weirs rested on sill position and depths ranged between 5.22 and 5.58 (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 and depths measured between 7.94 and 8.48 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.08 and 6.20 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.7 and 2.0 fps near the SSE and 2.6 and 3.0 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 0.7 and 1.3 fps.  

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period. 

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Surface debris in the immediate forebay area was not observed during this report period.  Gatewells remain clear of debris. 

Spillway Weir:  The weir was operated in the high crest position (622 ft.) spilling approximately 7200 cfs through August 5 at 0822 hours when it was removed from service.  The uniform spill pattern across spillway 2 – 8 was implemented shortly after the weir was removed from service.    
ESBS/VBS:   All operating ESBS were within criteria during this report period.  
Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection channel continued to operate with 23 open orifices – no problems to report. 

Transportation Facility:  Collection and transport continued through this report period.  Daily collection ranged between 753 and 1,568 for a total of 8,690 for the week.  All fish were transported except for mortalities.  Descaling and mortality rates for this report period are 0.2% and 0.9% respectively.
The facility switched to back-up diesel generator power on August 3 at 0958 hours in support of power line outage maintenance, doble testing and transformer repairs.  On August 4 the generator was removed from service from 1530 to 1550 hours for maintenance.   

Transport Summary:  All barge transport operations were successfully completed without incident.    
River Conditions

On August 5 at 1644 hours, minimum operating pool upstream of Little Goose Dam was increased to range between 633.5 and 634.5 ft. to support navigation safety.

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	40.8
	34.0
	12.3
	10.2
	70.7
	69.1
	6.0
	5.8


*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling Water Strainers were not inspected this report period. 
Invasive Species:  The Zebra Mussel substrate monitor was inspected on August 5, no mussels were observed.  The next inspection for zebra mussels is scheduled for September 1.  

Avian Activity:  Up to 10 gulls and 5 cormorants were observed in the vicinity of the dam during this report period. 
Project:  Lower Granite

Biologists:  Mike Halter and Ches Brooks 
Dates:  July 30 – August 5, 2010

Turbine Operation

Lower Granite had turbine units 1, 2, 4, and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remained out of service for a rewind and will not be available until approximately December 31, 2010.  Turbine unit 5 returned to service after annual maintenance on August 4 at 1548 hrs.  Turbine unit 1 was out of service on August 5 from 0907 until 1024 hrs, for 3D cam calibration.  Summer spill operations began on June 21 and is slated to continue through August 31.

Adult Fish Passage Facility

On July 31 and August 1-3 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  

Fish Ladder:  All criteria were met during the inspections.

Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances this week.  Weir depths at the south shore fishway entrances were on sill during the July 31 inspection with depths of 7.8 feet on both gates.  South shore entrance weir depths on the August 1-3  inspections were above the 8.0 foot criteria level due to tailwater elevations above 633.0 feet.  North powerhouse fishway entrance weirs were on sill all week due to tailwater elevations below 636.0 feet.  Weir depths at the north powerhouse entrances ranged from 5.1 to 5.5 feet.  Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 5.0 and 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.87 to 1.01 feet per second and averaged 0.93 feet per second.

Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.  
Juvenile Fish Passage Facility

The juvenile fish sample rate was increased from 20% to 50% at 0700 hours on August 1.  The sample system was set to “divert during sample mode” at 0700 hours on August 4.

Forebay Debris/Gatewell Debris/Oil: Debris levels were low during the week.  It was not necessary to hand-dip debris from any gatewells this week.  No evidence of oil was found in any of the gatewells.
ESBSs/VBSs: The last video inspections were conducted on June 26 and 27.  No additional problems were detected.   The next video inspections are scheduled later in August.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Debris levels remained very light during the week.  Collection gallery orifices were back flushed every three hours around the clock to ensure they remained free of materials that might impede fish passage.   
Transportation Facility:   Fish numbers remained relatively low during the week.  Consequently direct loading activities did not take place.  All facets of facility operation went smoothly. 
Transport Summary:  Fish are being barged on the even days of the month.  Barge transport operations from McNary Dam began on July 16 and continue to go smoothly.  
Removable Spillway Weir:   The RSW remains in service and is operating satisfactory.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	43.4
	36.2
	18.7
	18.6
	67.5
	65.9
	5.0
	5.0


*Cooling line intake temperature.

Other
Inline Cooling Water Strainers:  Inspection of the inline cooling water strainers took place on August 5.   No lamprey were found during the inspection.  The next inspections will take place in mid to late September.
Invasive Species:   The zebra mussel trap at the adult fishway exit was examined for zebra mussels on the Aug 2 inspection.  No evidence of zebra mussels were found.

Research:  The adult fish trap continued operation at a 4% sample rate during the week.  Unmarked Chinook are being PIT-tagged and scale and tissue samples are being taken.  One out of every seven hatchery Chinook is being scale sampled.  All hatchery coded wire tagged Chinook are being scale sampled.  Wild steelhead are being PIT-tagged and one out of every 11 hatchery steelhead is being scale sampled.  The collection of American shad for genetic analysis has concluded for the season.  Water temperatures in the trap have been in the upper 60°F range but so far have remained below 70°F.

Sockeye transport operations by Idaho Fish and Game concluded on July 15.  A total of 19 adult sockeye were transported to Eagle Fish Hatchery (11 females, 8 males) and there has been no reported mortality.

