U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#05-2011
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: March 25 - 31, 2011
Turbine Operation

McNary had 11 to 12 turbine units available for power generation this week.  Turbine units 2 and 7 remain out of service for the rewind contract which should be completed by the end of May.  On March 31, turbine unit 10 returned to service after repairs and testing.  On March 28, turbine unit 1 was out of service for 9.2 hours for pre-rewind testing.  The next day, turbine unit 1 was again taken out of service one hour to remove test equipment.  On March 30, turbine unit 6 was out of service four hours for tapping the hub.  On March 28, 29 and 31, turbine units 3 through 6 and 8 were out of service a total of 19.2 hours for trash rack cleaning.  The speed switch in turbine unit 6 was also repaired during this outage.  On April 1, the hard constraint one percent criteria will begin.      

Adult Fish Passage Facilities 

On March 27, 30 and 31, the McNary fisheries biologist performed measured inspections of the adult fishways.  On March 31, the picketed leads were lowered at both exits.  Adult fish counts will resume on April 1.                
Fish Ladders:  Both ladders met all Fish Passage Plan criteria were during measured inspections.                  

Fishway Entrances and Collection Channel:  The Washington ladder met all and the Oregon ladder met most inspection point criteria.  On March 27 and 31, the south Oregon entrance, SFEW1 measured 8.8 and 8.9 feet respectively.  These discrepancies were likely measurement drifts from hydraulic gradients created by involuntary spill.  All other Oregon inspection points were in criteria.  Collection channel velocities averaged 1.7 feet per second.   

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees. On March 29, pump 1 was taken out of service for 20 minutes in support of grease pump service and maintenance.  Otherwise, pumps 1 and 3 remained in continuous service.  Pump 2 remains out of service for major overhaul including upper and lower bearing replacements.  Pump 2 is now expected to remain out of service until approximately June 30 as significant bearing and shaft alignment issues were recently discovered.  On March 27, the juvenile facility returned to service, supplying 450 cfs to and improving the north powerhouse pool differential.  This supply of water was interrupted for 8 hours on March 31 when the juvenile fishway was temporarily taken out of service (see section below for more details).      The Wasco County PUD turbine unit tripped out of service three times for unknown reasons on March 29 and 30.  Outage times totaled 6.8 hours.  The bypass system functioned well during the PUD outages.  

Juvenile Fish Passage Facility

Primary bypass operations began March 27 when the system was “watered up”.  Collection channel issues may delay the start of alternating days of primary and secondary bypass (described in more detail below).  There are no other major facility problems to report. 

Forebay Debris/Gatewell Debris/Oil:  Moderate to heavy forebay debris accumulations were observed this week depending on flow patterns and wind direction.  Trash rack differentials measured from 1.9 to 5.2 feet on March 28 at turbine units 4, 6, 8 and 12.  On March 30, turbine unit 5 trash rack differential readings reached as high as 4.3 feet.  On March 28, 29 and 31, approximately 27.5 cubic yards of debris were removed from trash racks associated with turbine units 3 through 6 and 8.  Most of the debris consisted of tumble weeds and wood.  During the last two weeks, all turbine unit trash racks except for those associated with turbine units 2 and 7.  Both of these turbine units have been out of service since July 2010.  Turbine unit 5 trash racks were raked twice during the last 2 weeks.  No juvenile lamprey mortalities were recovered from the trash racks this week.  No problems were observed in the gatewell slots during this report period.  Differential monitoring efforts will continue.
ESBSs/VBSs:  All ESBS’s remain raised and maintenance has almost concluded.  The project plans to install the screens from approximately April 4 to 14 similar to the last two seasons for juvenile lamprey passage.  On April 4, fish screens in units out of service will be installed then work will begin with operational units on April 5 as outlined in the Fish Passage Plan.  When fish screen installation begins, VBS monitoring will resume.           

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  From 0830 to 1130 hours on March 27, the collection channel was placed into service on March 27.  All systems were placed in automatic operation and 42 orifices were opened.   On March 27 and 30, a total of 43 orifices were in service due to reduced flow from orifices associated with turbine units 4 and 5.  Normal orifice flow in these turbine units resumed, following trash rack raking the next day.  The orifice count was then reduced to 42.  No orifice blockages were observed.  
On March 27, the rectangular screen cleaning mechanism triggered a timing alarm.  An adjustment of a limit switch resolved the issue.  A drive motor failed the next day forcing the same cleaner out of service.  On March 31 from 0715 to 0830 hours, the collection channel was partially dewatered to allow closer inspection and repairs.  Flow was temporarily routed out the emergency bypass.  Electricians determined that repairs were not possible and a replacement motor was needed.  Unfortunately a replacement motor was not available and the collection channel was returned to primary bypass mode.  A new motor was expeditiously ordered.    
On March 28, the transition screen cleaning brush also triggered an alarm.  Normal operation resumed after the alarm was reset.  The same day, facility personnel noted problems with the powerhouse air supply.  Because the transition screen requires air for part of its function, the mechanism was turned off until the air supply issue could be resolved.  
Since March 28 during primary bypass operations, fisheries technicians have been manually operating the air burst system hourly on a 24 hours/day to keep both screens from becoming obstructed.  Secondary bypass operations are not feasible until the rectangular dewatering screen is repaired.  The facility does not have enough staff on hand to simultaneously monitor the channel and operate the collection/sampling facility at night.  
There is nothing else to report this week other than the re-lamping of orifice attraction lights on March 29.

Transportation Facility:  As mentioned above, the facility was placed into service and operated in primary bypass mode.  Bypass operations were interrupted due to collection channel activities described above.  All systems will remain “off” until alternating days of primary and secondary bypass begin.  There were no facility specific problems to report other than the bird hazing sprinkler cannon being jammed with debris.  Normal bird cannon operation was restored March 28, when the water supply line was flushed with air.                  

Transport Summary:  There is no transport taking place at this time.

River Conditions

River conditions during the week are outlined in Table 1 as provided by the control room.  Data periods run from 0000 hours to 2400 hours each day.  Due to river flow in excess of powerhouse capacity, involuntary spill occurred all week.  The project plans to install the spillbay weirs before April 10.      

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	245.6
	210.2
	70.7
	47.7
	42
	41
	3.4
	     2.3


*Unit 1 scroll case temperature.

Other

Inline Cooling Water Strainers:  On March 28, the cooling water strainer associated with turbine unit 1 was examined.  Three juvenile lamprey mortalities were recovered.  The next complete examination of main units cooling water strainers will occur in mid-April.       

Invasive Species:  The next detector inspection will take place in mid-April.  
Bird counts resumed March 27.  No birds were noted in the forebay which was checked once a day.  Tailwater locations were checked twice a day.  The highest tailrace counts included 20 cormorants and an occasional gull in the spill basin.  
The adult fallback study continued.  Other researchers are preparing for the upcoming season.  
Project:  Ice Harbor

Biological Technician: Steve Jeffers
Dates: March 25 - 31, 2011
Turbine Operation
Turbine units 1, 2, 3, 5, and 6 were available for operation this reporting period.  Turbine units 1, 2, 3, 5, and 6 were out of service for short periods on March 28 and 29 for turbine unit trash rack raking.  Turbine unit 1 remained out of service March 29 to March 31 due to a STS picking beam being stuck in gatewell slot 1B during screen installations.  Turbine unit 1 returned to service April 1.  Turbine unit 4 remains out of service for blade repair.     

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fishways March 28, 29, 30, and 31. 
Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.3 feet, off sill with 8.0 feet, off sill with 8.2 feet, and off sill with 8.5 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.1 feet, off sill with 7.4 feet, off sill with 7.8 feet, and off sill with 8.3 feet.  The north shore entrance (NSE) was off sill with a depth of 9.4 feet, off sill with 9.5 feet, off sill with 9.5 feet, and off sill with 9.9 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The out of criteria NFE readings were reported to the shift operator.  Adjustments were made with the adult fishway controls to lower the NFE back into criteria.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  All north shore fish pump are in service.  Five of 8 south fish pumps are available for service.  South fish pump 1 is out of service due to vibration, south fish pump 3 is out of service due to gearbox problems, and south fish pump 8 is on stand-by.  
Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay in front of the powerhouse.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  Turbine unit trash rack raking occurred this reporting period.  Approximately 35 yards of debris was removed with the majority being removed from turbine units 1 and 2.  

STSs/VBSs:  Turbine unit 1 STS installations began March 29.  The STS picking beam became stuck in gatewell slot 1B during screen installation.  The beam was removed March 31.  Other than the previously deployed screen in slot 1A, all STSs were successfully installed April 1.  STSs  are being operated in cycle run timing mode.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.  
Juvenile Bypass Facility:  The bypass was placed into operation March 23.

Fish Sampling:  The first sample is scheduled for April 11.  Sampling days will be Monday and Thursday through the beginning of July.

Removable Spillway Weir:  The RSW is in operation for involuntary spill.  Spill for fish will begin April 3, 2011.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	112.9
	77.7
	49.0
	1.9
	45
	43
	3.1
	2.4


*Unit 1 scrollcase temperature.
Other

Inline Cooling Water Strainers:   Cooling water strainers were last inspected March 8.  A total of 13 juvenile lamprey and 3 juvenile shad mortalities were recovered. 
Invasive Species:  No zebra mussels were observed during this report period.

Project:  Lower Monumental Dam

Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: March 25 - 31, 2011
Turbine Operation

All turbine units are being operated in soft constraint of the 1% operation criteria.  BPA requested involuntary spill began March 30.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on March 27, 28 and 30.   

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  Picketed leads were in the raised position until the 28th when the north side leads were lowered by hoist.  Lack of a crane operator kept the south side from being lowered until April 2.

Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  

SPE 1 and SPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.    

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Auxiliary Water Supply System (AWS):  All AWS pumps were in service and operating throughout this period.   

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 992 square yards of forebay debris observed during this period.  

STSs/VBSs:  STSs are operating in cycle mode.      

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass was watered up on March 14 at 1520 hours.   
On Sunday, March 27 at 1215 hours, a debris pile from the primary dewaterer lodged in the upper pipe section just below the bypass flume.  Weirs at the primary dewaterer were lowered to dewater the flume so that the debris could be removed.  Orifices were left open during the debris removal.  At 1345 hours the plug had been removed and the weirs were manually adjusted to resume flow in the flume.

The problem turned out to be the PLC (Programmable Logic Circuit) controller not being in service.  Electricians were called out and the issue was quickly resolved.  The PLC is required to control both the mechanical and pneumatic cleaners within the primary dewaterer.  Juvenile fish mortalities included 22 clipped yearling Chinook, and 5 clipped steelhead.  Adult fish mortalities included 3 clipped hatchery steelhead, and 5 peamouth.  Approximately 17 juvenile fish were released alive (species unknown).

Collection Facility:  The facility was watered up for testing on March 28.      

Transport Summary:  No collection for transport occurred this reporting period.  

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	88.8
	77.0
	3.7
	0
	44.5
	44.0
	2.6
	2.4


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers:   Cooling water strainers were last inspected March 3.  Forty-three lampreys and 4 Siberian prawns were recovered.  

Invasive Species:  There were no zebra mussels observed at the monitoring stations on March 24. 

Project:  Little Goose

Biologist: George Melanson
Dates: March 25 - 31, 2011
Turbine Operation

Turbine units 1 through 6 were available for service this report period except for the following outages.  Turbine unit 4 was removed from service on March 28 at 0730 hours to March 30 at 1315 hours for Governor Maintenance and Training.  Turbine unit 6 was removed from service on March 28 from 1102 to 1650 hours to install fish screens. All available turbine units were operated in soft constraint of the 1% efficiency criteria.
Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway on March 28, 30 and 31.
Fish Ladder:  The ladder exit head differentials ranged between 0.1 and 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs measured 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady a 0.0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler located at the ladder exit to force debris away operated satisfactorily.

Fishway Entrances and Collection Channel:  Most fishway measurements were in criteria during inspections.  Channel to tailwater head differentials ranged between 1.18 and 1.96 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.44 and 8.82 feet (criteria ≥8.0 ft), NPE 1 and 2 ranged between 7.18 and 7.33 feet (criteria ≥7.0 ft or on sill) and NSE weir depths ranged between 8.0 and 8.3 feet (criteria ≥ 6.0 ft.).  Collection channel water velocities (criteria 1.5 fps) ranged from 1.5 and 1.7 fps near the SSE and 1.8 and 2.4 near the NSE.  Subsurface water velocities near the SSE (flowmeter) electronically reported 0.6 fps on all three inspections.   

Auxiliary Water Supply System:  All fish pumps operated in criteria.  

Juvenile Fish Passage Facility
Forebay Debris/Gatewell Debris/Oil:  Up to 5,400 square feet of floating debris was accumulated inside the trash-shear boom.  Small amounts of debris were removed from gatewells.  

Spillway Weir:  The spillway weir was not in service during this report period.
ESBS/VBS:  ESBS associated with turbine unit 6 were lowered into position on March 28.  All ESBS operated within criteria this report period.   
Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated in criteria with 21 open orifices. 

Transportation Facility:  The juvenile fish facility was watered-up on March 29, no problems to report.
Transport Summary:  Transport operations are expected to begin in late April or early May. 
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	100.1
	71.8
	12.6
	4.2
	45.8
	43.7
	3.2
	3.0


*Ladder temperature.

Other

Cooling Water Strainers:  On March 24, cooling water strainers were inspected.  Four juvenile lamprey mortalities were removed.  

Invasive Species:  The Zebra Mussel substrate monitor is scheduled for inspection on April 5.  

Avian Activity: Up to 20 gulls and the occasional cormorant were observed this report period. 
Project:  Lower Granite

Biologists:  Mike Halter and Ches Brooks 

Dates: March 25 - 31, 2011
Turbine Operation

Lower Granite had turbine units 1, 2, 4 and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remains out of service for a rewind and the estimated return to service date is now April 29, 2011.  Turbine unit 5 is out of service for stator repair and the estimated return to service date is May 13, 2011.    
Adult Fish Passage Facility

On March 26, 27, and 28 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system. Video counts in the adult fish ladder are to conclude on March 31.  Videos counts began March 1 with recording time set from 0600 to 1600 hours.  Visual counting between the hours of 0400 and 2000 begins on April 1.
Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were also within criteria on all inspections this week (criterion ≥ 8.0 feet).  Both north powerhouse fishway entrances were on sill during the week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 6.6 to 7.1 feet. Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 4.8 and 5.2 feet on both gates (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.94 to 1.13 feet per second and averaged 1.01 feet per second.

Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week. 
Juvenile Fish Passage Facility

Juvenile fish sampling (only) began on March 25 at 0700 hours, with a sample rate of 10%.  The first sample was worked up in the lab on March 26.   Due to relatively high numbers of fish, the sample rate was reduced from 10% down to 4% at 0700 hours on March 29.  The sample rate was reduced again from 4% down to 2% at 1900 hours on the evening of March 29 (half the way through the 24 hour sample) due to the concern over having too many fish in the sample.  On March 30 the sample rate was increased to 4%.  On March 31 the sample rate was again decreased to 2%.
Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week; none was removed.   

ESBSs/VBSs: ESBS installations took place the week of March 21.  There were no problems with fish screens during the report week.  ESBS video inspections are scheduled for April 22-23.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Orifices are being backflushed every three hours around the clock to ensure they remain free of materials that might impact fish passage.
Transportation Facility:  General transport operations are uncertain at this time but will probably start in very late April or early May due to the above average snowpack conditions.  The first research barge is tentatively scheduled to depart on April 7.  Juvenile fish sampling (only) began March 25.
Transport Summary:  No transport operations took place this week.

Removable Spillway Weir:   Nothing to report on the RSW.  
River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	108.7
	77.3
	19.9
	0.0
	47.5
	46.8
	3.1
	2.6


*Scrollcase temperature.

Other
Inline Cooling Water Strainers:  Lamprey inspections were conducted on March 30-31.  A total of 17 lamprey mortalities were removed from the strainers.
Invasive Species:  The zebra mussel trap at the adult fishway exit was replaced with a new trap using scrub pad material on March 7.  The old trap was refurbished with new net mesh material and was deployed on March 9.  Both traps will be utilized this season

Research:  The adult fish trap operations continued with sample rates set at 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All captured unclipped steelhead are being PIT-tagged.  Scale and genetic samples are also being taken from these fish.  Previously PIT-tagged steelhead (either clipped or unclipped) will have both scale and genetic samples taken for verification purposes.  
Idaho Department of Fish and Game (IDFG) personnel conducted genetic stock identification work on Chinook and steelhead smolts from the lab during the week.  The goal of the study is to enumerate and characterize the natural production of yearling spring/summer Chinook salmon and steelhead above Lower Granite with regard to age composition and genetic stock identification.  IDFG will sample every day until the first part of July with a goal of collecting between 2,000 and 4,000 genetic samples each from yearling spring/summer Chinook and steelhead and 500-1,500 genetic samples from subyearling fall Chinook. 

