U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#21 - 2011
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: July 15 - 21, 2011
Turbine Operation

McNary had nine to 10 units available for power generation this week.  Units 1 and 10 remain out of service for the rewind contract which will be completed in approximately six months to one year.  Unit 7 remains out of service until approximately July 23 for field testing.  As part of the unit 7 testing, unit 8 was out of service until July 19.  Both units were intermittently run on July 16 during the testing.  From July 18 to 21, unit 2 was out of service for annual maintenance.  Later in the day, due to the ESBS in 2A slot failing, the unit was again removed from service.  Repairs to the ESBS will be completed on July 22 returning the unit to service.  On July 19, unit 9 was out of service for ESBS camera inspections for 20 minutes.  During the inspection, the ESBS in 9C slot was found failed removing the unit from service until it could be replaced on July 20.  Also, that day, unit 8 was in and out of service for approximately two hours until electrical issues could be resolved.  By July 19, all hydraulic fluid which was reported last week had been removed from station service unit 01 and its headgate had been repaired.                 

The hard constraint one percent criterion continues with units very briefly running outside the criteria on July 17 due to a programming issue.  From July 19 to 20 for unit 14 and from July 21 to 22 for units 4, 8 and 9, the units’ load had to be reduced to the lower limit of the criteria due to high VBS differentials.          

Adult Fish Passage Facilities 

On July 15, 18, and 20, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting including video review for lamprey, water temperature monitoring, and nightly lowering of Oregon entrance weirs, NFEW2, NFEW3, SFEW1 and SFEW2, for lamprey passage continue.    

Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.    
At the Washington ladder’s exit, debris in the area has decreased.  The picketed leads continue to be monitored by all personnel.  On July 17, the fisheries staff cleaned the leads.       

At the Oregon exit, measured differential readings revealed no problems with the traveling screens.  The regulating weir alarm triggered once and was reset.  

Fishway Entrances and Collection Channel:  On July 20, Washington ladder entrance weir, W3, measured 7.2 feet.  The technical staff is examining the possibly of a programming issue causing the calibration drifts noted at W2 and W3 in the past.  All other inspection points on both ladders were in criteria.  The Oregon ladder’s south powerhouse entrance weir, SFEW2, has a failed LED which has not yet been replaced.  Until then, the dial indicator on the weir’s cable drum will be used for measurements.  The collection channel velocity averaged 1.7 feet per second.     

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of approximately 30 degrees with no interruptions in service recorded.  Pump 2 remains out of service due to a major overhaul.  The project now estimates the return to service date to be January 31, 2012.  

The juvenile facility continues to supplying the usual 450 cfs to the north powerhouse pool with no interruptions in service.  Finally, the Wasco County PUD unit was out of service from approximately 0000 to 0500 hours every night from July 15 to 18 due to BPA not requiring the power production.  During all outages, the bypass system operated well.  

Juvenile Fish Passage Facility

Alternating days of primary and secondary bypass concluded at 1200 hours on July 20 when collection for barge transport began.  No interruptions in the bypass schedule or collection occurred this week.  

For the report week, 258,881 smolts and 1,000 juvenile lampreys were enumerated.  For the smolts, 197,438 were bypassed and 52,772 were transported.    

Forebay Debris/Gatewell Debris/Oil:  During the week, forebay debris remained light.  However, debris continues to be monitored through out the project with most debris being on the upstream face of the spillway.  Trash rack differential monitoring revealed no significant problems and no racks were cleaned.  Repairs to the damaged trash rack hoist and cleaning device continue with a completion date of August 18 being set.                 

No problems were seen in the gatewell slots.  The slot at 1B remains dewatered as the issue with the headgate for that slot has not yet been resolved.         

ESBSs/VBSs:  ESBSs are deployed in all units except at 1B and 10B slots.  Rehabilitation continues on the two spare ESBSs.  The screens at 2B, 3B and 13A slots remain in bypass mode.  On July 19, ESBS camera inspections at units 8 and 9 along with the screen at 2C slot (which had yet not been examined) revealed that the screen in 9C slot had failed.  There was no indication of a problem since then last inspection on May 24.  However, this screen had been in bypass mode.  The screen was coated in milfoil and fine debris but no fish mortalities were seen.  The screen was replaced the next day.  On July 21, the screen in 2A slot which had been in transducer bypass mode failed.  The electrical cable was repaired the next day.  

VBS monitoring revealed nine screens out of criteria.  For the week, six of these screens were cleaned along with three others.  The other three high screens were cleaned on July 22.  As mentioned above, four units were de-rated over night until the screens could be cleaned the next day.  The project has 10 to 12 VBSs scheduled for rehabilitation and replacement this year.        

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Forty two orifices were used this week with no blockages observed.  Since 1B slot is dewatered, a make-up orifice has been opened at 1C slot.              

All system operated well in automatic mode.  Besides during primary bypass and daily checks, the channel was also monitored during VBS cleaning.  

Transportation Facility:  Alternating days of primary and secondary bypass concluded at 1200 hours on July 20 when collection for barge transport began.  Before this date, all bypass systems operated well as outlined in previous reports.  Smolt monitoring will occur daily during the transport season. The primary PIT tag system was also activated to run continuously at the start of transport operations.  The CRITFC study equipment that was installed in the primary A side PIT sample tank was removed just before collection began.  The PIT tag equipment continues to receive weekly checks.  The secondary (C and D) PIT/bypass gates remain off and closed for collection.  Finally, for collection, the sample gates will remain activated for continuous operation.  

Ice block checks of the return to river lines during bypass season and balloon test of the PIT tag lines during collection revealed no problems.                               

Work on a tailscreen hoist for the east raceway bank and fabrication of the new raceway tailscreens that will pass juvenile lamprey continues.    

Transport Summary:  The first barge was loaded on July 21 with no problems to report.      

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Clarity data was provided by the control room.  The summer spill program, which designates 50 percent of total flow to be spilled, continues.  Actual spill ranged from 57 to 64 percent of total flow due to high discharge in excess of powerhouse capacity.  Before and after barge loading operations, spill will be briefly closed so the fish tug and barge can go to and from the juvenile fish facility safely.      

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	337.5
	283.0
	215.6
	159.9
	62.7
	61.2
	4.6
	     5.3


On July 21, spill gate 1, returned service. The crane which moves the gate has issues which should be resolved early next week so the bay can be opened.        

The smolt monitoring staff continues to gather water temperature data which will be reported in a separate report. 
Other

Inline Cooling Water Strainers:  The next cooling water strainer examination will occur in late July.  

Invasive Species:  The next zebra mussel station examination will occur in early August.         

Predatory Bird Observations:  Bird counts continue with the forebay area being checked once a day and the tailwater area being checked twice a day.  In the tailwater area, high counts were 88 gulls, 16 pelicans, 17 cormorants and 40 terns.  Most birds were seen in the spill basin with the pelicans along the navigation lock wall apparently feeding on adult shad.  Bypass outfall high counts were five gulls, two terns and six pelicans.  Pelicans were also observed by the adult return outfall.  The water cannon operated well.  Swing shift noted the most activity.  The bird hazing contract concluded on July 16.     

In the forebay area, the high count was four juvenile gulls with an occasional pelican or osprey observed.  No grebes were seen on project.  The number of pelicans roosting on the rocks by the Washington boat dock has decreased.  

Research:  The study of the Oregon ladder exit area by the traveling screens continues with the fisheries staff no long assisting in monitoring the debris trap due to the start of transport operations.  Preparations for the adult lamprey passage study are also in progress with camera installation at entrance weir SFEW2 planned for next week.  Gas bubble trauma examinations continue and results can be requested from the smolt monitoring staff.  The ODFW angling survey for small mouth bass in the project tailwater and forebay adjacent to the powerhouse also continued.  Finally, the CRITFC study designed to monitor PIT tagged fish with cameras concluded on July 20 with the start of transport collection.    

Project:  Ice Harbor

Biologist: Mark Plummer

Biological Technician: Stephen Jeffers
Dates: July 15 - 21, 2011
Turbine Operation
Turbine units 1, 2, 5, and 6 were available for operation this reporting period.  Turbine unit 3 remains out of service for annual maintenance.  Turbine unit 4 went out of service July 12 at 0659 hours for scheduled Doble testing and required cleaning of the transformer and buss work insulators on line 2.

Adult Fish Passage Facilities

Fish facility personnel inspected the adult and juvenile fish passage ways July 18, 19, 20, and 21.
Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.  The current method of monitoring the velocity is channel/tailwater differential, floatation device timing, and visual observation.
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.9 feet, off sill with a depth of 8.6 feet, off sill with a depth of 8.7 feet, and off sill with a depth of 8.5 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.0 feet, off sill with a depth of 7.8 feet, off sill with a depth of 8.9 feet, and off sill with a depth of 9.2 feet.  The north shore entrance (NSE) was on sill with a depth of 11.0 feet, on sill with a depth of 10.7 feet, on sill with a depth of 10.7 feet, and on sill with a depth of 11.1 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The entrance weir depth out of criteria at the NFE on July 19 was reported to the shift operator to make adjustments.  All channel/tailwater differentials were in criteria, except July 20.  On this inspection, the visual north adult fish ladder channel/tailwater elevation was 0.9 feet and the computer indication was 0.84.  This cannot be adjusted as the north adult fish entrance weir lifting mechanism has failed.  The adult entrance weir has fallen to sill at 332.2 fmsl.  High river flows are maintaining adult passage criteria at this entrance.  Plans are to repair the entrance hoisting mechanism when the water flows drop off.  Channel/tailwater differential criteria are 1 – 2 feet.  Repairs will be made when river flows lower and access to the entrance weir can be accomplished.
Auxiliary Water Supply System:  Normally, 2 of the 3 north shore fish pumps are operated.  All north shore fish pumps were available for operation.  South shore fish pump 1 remains out of service due to vibration issues at the gearbox shaft.  South shore fish pump 3 was out of service July 20 from 0949 hours to 1408 hours to uncouple the motor for repairs to prevent excessive vibration.  Currently, 6 of 8 south shore fish pumps are operating.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay.  Fish ladder exits are clear of debris and the bubblers are operating.  

STSs/VBSs:  The STS rotations are in continuous run mode as the average length of both the subyearling Chinook and the migratory sockeye being below 120 mm.  No problems were observed on the July STS inspections.  August STS inspections are scheduled for August 9 and 10.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.  
Juvenile Bypass Facility:  The bypass was placed into operation March 23.

Fish Sampling:  Fish sampling for the 2011 season concluded July 7.

Removable Spillway Weir:  The RSW is in operation.   

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	92.2
	74.5
	62.0
	51.1
	63
	62
	4.0
	2.6


*Unit 1 scrollcase temperature.
Spill for fish began April 3, 2011.

Other

Inline Cooling Water Strainers:  No fish were found during the last inspection on June 21. 

Invasive Species: No zebra mussels were observed during this period.

An adult clipped Steelhead mortality was found July 21 on the walkway in the juvenile collection channel.  This appeared as though the fish attempted to jump back into the orifice but had cleared the orifice, railing, and netting and desiccated on the walkway.
Project:  Lower Monumental Dam

Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: July 15 - 21, 2011
Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.  Unit 6 was taken out of service for annual maintenance on June 28 at 0701 hours and returned to service on July 21 at 1350 hours.  Unit 3 was out of service on July 21 from 0555 hours to 0735 hours due to XJ-3 fan failure and from 0859 hours to 0909 hours due to an exciter brush failure. 
Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on July 15, 16, 17 and 20.   

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel:  NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections. 

SPE 1 and SPE 2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.1’, 7.6’, and 6.9 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.
SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections with the exception of a 7.5 feet reading on July 15.  This was due to the gate not responding in remote mode.  The gate was lowered to the sill position in local mode immediately following the inspection.  While on sill the gate depth readings were 7.9’ and 7.5 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Auxiliary Water Supply System: All AWS pumps were rotated out of service on July 18 and 19 for annual maintenance.  Pumps 2 and 3 were taken out of service on July 18 from 1345 hours to 1410 hours to blow out the AWS turbine penstock.  All pumps were in service and operating for the remainder of this period.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 800.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-12% surface coverage.  No oil was observed in gatewells.
STSs/VBSs:  STS operation remained in continuous run mode as average fork length of sub-yearling Chinook and/or sockeye is less than 120mm.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20 orifices open.  The primary dewatering structure mechanical screen cleaner continues to malfunction when set in automatic operation mode.  The problem was found to be that the metal connector attaching the electric motor to its brake assembly is broken.  Replacements have been ordered.  The bubbler screen cleaner has been set to cycle every 10 minutes. It is generally adequate for keeping the screen clean.  The mechanical screen cleaner is being operated manually on an hourly basis in addition to the bubbler system due to high levels of leafy debris. 
Collection Facility:  No problems occurred this week.  

Transport Summary:  Alternate day transport is occurring with barges arriving on even numbered days.  

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	86.8
	69.4
	17.4
	16.9
	64.0
	62.5
	3.4
	3.1


*Scrollcase temperatures.

Other

Inline Cooling Water Strainers: Cooling water strainers were inspected on July 5.  No live lamprey was recovered.  Mortalities included 23 lamprey, 0 salmon smolts, 0 juvenile steelhead, 0 Siberian prawns, and 11 shad.

Invasive Species: There were no zebra mussels observed at the monitoring stations on July 1. 
Pelican presence at the bypass outfall has been infrequent.  
Project:  Little Goose

Biologist: Rick Weis
Dates: July 15 - 21, 2011
Turbine Operation

Turbine units 1 through 4 and 6 were available for service throughout the report period.   Turbine unit 5 was returned to service on July 21 at 1410 hours following completion of annual maintenance.  All turbine operations were within 1% of best efficiency.  
Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway July 15, 19 and 21.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs remained steady at 1.0 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials measured no differential on all three inspections (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.04 and 2.12 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.04 and 8.66 feet (criteria ≥8.0 ft), NPE weirs were on sill and depths ranged between 5.66 and 5.96 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 5.76 and 6.04 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.3 to 2.1 fps near the SSE.  NSE was not recorded this week due to closure of North shore area.  

Auxiliary Water Supply System:  All fish pumps operated in criteria.  
Juvenile Fish Passage Facility
Forebay Debris/Gatewell Debris/Oil:   Up to 8,400 square feet of woody debris remains in front of the turbine intakes.  Small debris continued to be problematic in a few gatewell orifices and hand removal of debris continued from gatewells.  

Spillway Weir:  The spillway weir continued to operate in the low crest position. 
ESBS/VBS:   All ESBS operated within criteria this report period.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated in criteria with 22 open orifices.  Increased orifices inspections and back-flushing continued.   

Transportation Facility:  Daily collection for this period ranged between 2,490 and 7,940 for a total of 33,542 for the week.  All fish were transported except for mortalities and several fry that were bypassed.  Descaling and mortality rates for this report period are 0.04% and 0.30% respectively.

Transport Summary:  Every other day barging operations were successfully performed this report period.
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	88.7
	71.1
	26.3
	21.0
	63.7
	61.5
	5.2
	2.8


*Ladder temperature.
Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected during this reporting period.  

Invasive Species:  The Zebra Mussel substrate monitor was inspected on July 12.  No mussels were observed.  The next inspection is scheduled for August 10. 

Avian Activity: Up to 15 gulls and 5 cormorants have been observed in the vicinity of the dam.   
Project:  Lower Granite

Biologists:  Mike Halter and Ches Brooks 

Dates: July 15 - 21, 2011
Turbine Operation

Lower Granite had turbine units 1-5 available for power generation at the beginning of the report week.  Turbine unit 6 is undergoing exciter rehabilitation.  The tentative return to service date for this unit is August 19.  All operating units were run within the operational guidelines.    

Adult Fish Passage Facility

On July 16, 17, 18, and 20 the Lower Granite COE fisheries biologists performed measured inspections of the adult fishway system.  

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Problems developed with the weir motor and cable control system on north shore fishway entrance number 1 (NSE-1) on the morning of May 31.  Inspection revealed that the cable had broken and the weir gate had dropped to the sill.  The weir motor was also burned up.  A temporary adjustment was done on the weir gate by crane on June 7 and the gate was dogged off at 635.0 feet by cables.  This setting will be maintained until an A-frame and chain hoist system can be put in place to adjust the weir depth relative to the tailwater elevation.  Head differential readings remained within criteria during all fishway inspections this week. Weir depths at the south shore fishway entrances also remained within criteria on all inspections. Both north powerhouse fishway entrances were on sill during the week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet). Weir depths at the north powerhouse entrances ranged from 5.9 to 6.5 feet.  Weir depths at the north shore fishway entrances were out of criteria on all inspections this week.  The readings on NSE-1 were off the scale (due to the temporary cable fix) while the readings on NSE-2 ranged from 5.0 to 5.1 feet (criteria ≥ 7.0 feet).  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.79 to 0.96 feet per second and averaged 0.88 feet per second.

Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and two were run all week.
Juvenile Fish Passage Facility

The juvenile fish facility sample rate was increased from 5.0% to 10.0% at 0700 hours on July 20 due to a decrease in sub-yearling Chinook numbers. 

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed. 

ESBSs/VBSs:  The last VBS/ESBS video inspections were attempted on June 24-25.  They were cancelled due to near zero water visibility and concerns with the increased spill levels (due to the need to shut off units one at a time) increasing dissolved gas levels.  The next inspections have been moved up to August 5-7.  

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Vegetative debris levels remained fairly high this report week.  The separator inclined screen was thoroughly cleaned of debris between 0805 and 0830 hours the morning of July 16.  The bypass valve was opened all the way during this cleaning event.  On occasions of partial clogs the separator technicians were able to clear the screen with the power air rake tool that the maintenance staff developed.  

Transportation Facility:  The fish transportation facility operated well during the week despite debris issues.  Raceways were swept prior to barge loading and a considerable amount of vegetative material (mainly Elodea) removed.  The facility has continued utilizing the larger (lamprey friendly) mesh raceway tailscreens.   

Transport Summary:   Every other day fish barging proceeded according to schedule on the even days of the report week.  Operations went smoothly all week.  

Removable Spillway Weir:  The RSW operated normally as part of the spill plan.  

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	89.5
	72.3
	19.8
	18.5
	64.8
	63.3
	5.0
	3.8


*Scrollcase temperature

Other

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on June 27.  A total of 38 lamprey were found in the strainers over a combined run time of 3998.6 unit hours.  Unit 6 strainers were not inspected due to a B.P.A. request.  The next inspections are scheduled for July 27-28.   Much has been said recently about lamprey working past the separator valves and ending up in the river by way of the concrete bypass pipe at the base of the separator.  Once in the river, they are somewhat concentrated in the outfall pipe area and subject to avian predation.  While it would be difficult (if not impossible) to build separator control gates tight enough to prevent some lamprey from exiting the system, we believe other areas may be more of an issue. Our separator technicians report that they have seen gull numbers increase when sweeping raceways (to remove debris prior to barge loading operations).  Apparently the sweeping operations are dislodging the lamprey from the raceways.  With the larger mesh raceway tailscreens in place, lamprey are passing out of the raceways and back into the river through the raceway exit water.  In addition, a large amount of vegetative matter (mainly Elodia) has been passing through the separator and ending up in the raceways.  Lamprey can become entangled in this material and discharged back to the river when the material (bushels) is removed and put in the raceway exit water.   Fortunately debris dropped off considerably during the report week and raceway sweeping operations have been minimized. 

Invasive Species:  The zebra mussel traps near the adult fishway exit were examined for zebra mussels on the July 11 inspection.  No evidence of zebra mussels was found.

Research:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All wild steelhead and Chinook captured are being PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead or Chinook (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.  Scale samples are also being taken from one out of every three hatchery Chinook.  Sort by code Lemhi origin Chinook are being radio-tagged and scale and genetic samples taken. 

