U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#22 - 2011
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: July 22 - 28, 2011
McNary had 10 to 12 units available for power generation this week.  Units 1 and 10 remain out of service for the rewind contract which will be completed in approximately six months to one year.  On July 22, unit 7 returned to service from field testing.  Also, on July 22, unit 2 returned to service after the ESBS power cable for the screen in 2A slot was repaired.  From July 23 to 25, unit 2 was out of service for a failed ESBS in 2B slot which was replaced.  From July 25 to 28, unit 4 was out of service for transformer testing and maintenance.  Also, on those dates, unit 3 was out of service for this work and annual maintenance.  At unit 3, an installation issue was found which will delay the units return until August 2.  On July 26, unit 12 was out of service 10.2 hours so the oil head could be repacked during which time an ESBS camera inspection occurred.                   

The hard constraint one percent criterion continues with no units running outside the criteria.  From July 21 to 22, electrical loads for units 4, 8 and 9, were reduced to the lower limit of the criteria due to high VBS differentials.  On July 24, units 12 and 13 were briefly shout down in order to “burp” the units.  This procedure reduced VBS differentials, and allowed the units to run at regular electrical load as no general maintenance crew was available to clean the VBSs until the following day.            

Adult Fish Passage Facilities 

On July 23, 25, and 28, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting including video review for lamprey, water temperature monitoring, and nightly lowering of Oregon entrance weirs, NFEW2, NFEW3, SFEW1 and SFEW2, for lamprey passage continued.    

Fish Ladders:  During measured inspections, both ladders met all Fish Passage Plan criteria.

The amount of debris at the Washington ladder exit has decreased.  The picketed leads continue to be monitored by all personnel.  The regulating weir triggered an alarm once and was reset.  There was also one water level alarm which was reset.          

At the Oregon exit, measured differential readings revealed no problems with the traveling screens.  One differential alarm occurred which was reset.  The screen wash pump also triggered and alarm once and was reset.  

Fishway Entrances and Collection Channel:  On July 23 and 25, Washington ladder entrance weir, W3, measured 6.1 and 6.8 feet, respectively.  The technical staff is examining the possibly of a programming issue causing the calibration drifts noted at W2 and W3 in the past.  On July 23, the Oregon ladder south pool differential measured 0.9 feet possibly due to the entrance weirs running deeper than normal.  The south powerhouse entrance weir, SFEW2, has a failed LED which has not yet been replaced.  Until then, the dial indicator on the weir’s cable drum will be used for measurements.  All other inspection points on both ladders were in criteria.  The collection channel velocity averaged 1.6 feet per second.      

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of approximately 30 degrees with two interruptions  in service.  On July 22 and 28, pump 3 was switched to a different bus for a total outage of about one hour.  On July 25, a fish pump alarm was reset with no problem found.  Pump 2 remains out of service due to a major overhaul.  The project now estimates the return to service date to be January 31, 2012.  

The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool with no interruptions in service.  The Wasco County PUD unit also had no interruptions in service this week.   

Juvenile Fish Passage Facility

Fish collection for barge transport continued with no interruptions to report.    

For the report week, 577,100 smolts were collected and barged and 1,300 juvenile lamprey were enumerated.  

Forebay Debris/Gatewell Debris/Oil:  During the week, forebay debris concentrations increased from light to moderate.  Debris continues to be monitored through out the project with half of the debris being on the upstream face of the spillway.  Trash rack differential monitoring revealed no significant problems and no racks were cleaned this week.  Repairs to the damaged trash rack hoist and cleaning device continued with a completion date of August 13 being set.                 

No problems were seen in the gatewell slots.  The slot at 1B remains dewatered as the issue with the headgate for that slot has not yet been resolved.         

ESBSs/VBSs:  ESBSs are deployed in all units except at 1A, 1B and 10B slots.    Rehabilitation on the two spare ESBSs should be completed by late August.  The screens in slots 3B and 13A remain in bypass mode.  On July 21, the screen in 2A slot which had been in transducer bypass mode failed.  The electrical cable was repaired the next day and the screen now operated in transducer mode.  On July 23 a faulty coupler forced the screen in 2B slot out of service.  This screen was replaced on July 25 with the screen from 1A slot.  The screen that was replaced had been in transducer bypass mode.  On July 26, ESBS camera inspections at unit 12 revealed no problems.  

VBS monitoring revealed 16 screens out of criteria.  These and three screens that measured high differentials on July 21were cleaned along with nine other screens on July 22, and July 25 through 28.  The two high screens that were “sloughed off” on July 24 were cleaned July 25.  As mentioned above, three units were de-rated over night until the screens could be cleaned the following day.  The project has 10 to 12 VBS’s scheduled for rehabilitation and replacement this year.        

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Forty two orifices were utilized this week with no blockages observed.  Since 1B slot is dewatered, a make-up orifice was opened at 1C slot.              

All system operated well in automatic mode.  On July 25, the side screen cleaning device underwent scheduled maintenance.  Besides daily checks, the channel was also monitored during VBS cleaning.  

Transportation Facility:  Collection for barge transport continues with smolt monitoring occurring daily.  The primary PIT tag system is running continuously.  From July 26 to 27, the A side PIT count tank was draining slowly indicating a possible debris clog.  The system was flushed, returning the tank to normal operation.  No fish loss was noted.  Balloon tests of the PIT tag lines revealed no problems.  The PIT tag equipment continues to receive weekly checks.  The secondary (C and D) PIT/bypass gates remain off and closed for collection.  Sample gates remain in continuous operation.  Raceways are being switched daily in order to reduce stress on collected fish.  

The opening and closing of spill for the barge traffic to the juvenile facility dock does cause channel and separator flow fluctuations which are being monitored closely.  

Work on a tailscreen hoist for the east raceway bank was completed this week.  Fabrication of the new raceway tailscreens that will pass juvenile lamprey continues.    

Transport Summary:  Barges departed from McNary on July 23, 25 and 27 without incident.    However, the barge on July 25 was loaded from 1600 to 1900 hours instead of the morning due to towboat engine failure at Little Goose.  On July 28, a towboat returning a fish barge upstream lost power to both engines while entering the locks.  The barge hit the upstream sill wall of the navigation lock.  After cleaning the fuel system, the towboat was able to return to operation,  The barge was returned to Lower Granite and removed from service.  

Preparations for daily transport have begun in which trucks would be utilized on non-barge days.         

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Clarity data was provided by the control room.  The summer spill program, which designates 50 percent of total river flow to be spilled, continues.  Actual spill ranged from 50 to 56 percent of total flow due to high discharge in excess of powerhouse capacity.  Prior to and after barge loading operations, spill is briefly closed to allow safe towboat and barge passage to and from the juvenile fish facility.      

Table 1.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	276.9
	241.7
	153.0
	123.1
	64.5
	62.5
	5.1
	     4.2


On July 21, spill gate 1, returned service. On July 25, the crane which moves the gate also returned to service.          

The smolt monitoring staff continues to gather water temperature data which is reported separately.    

Other

Inline Cooling Water Strainers:  The next cooling water strainer examination will occur on August 2.    

Invasive Species:  The next zebra mussel station examination will occur on August 2.         

Predatory Bird Observations:  Bird counts continue with the forebay area being checked once a day and the tailwater area being checked twice a day.  In the tailwater area, high counts were 133 gulls, 18 pelicans, nine cormorants and 14 terns.  Most birds were seen in the spill basin with the pelicans along the navigation lock wall apparently feeding on adult shad.  By the bypass outfalls, an occasion pelican, tern, and gull were noted.  Pelicans were also observed by the adult return outfall.  The water cannon operated well.       

In the forebay area, the high count was 60 juvenile gulls with an occasional grebe, pelican or osprey observed.  No grebes were seen elsewhere on project.  The number of pelicans roosting on the rocks by the Washington boat dock has decreased.  

Research:  The study of the Oregon ladder exit area by the traveling screens continues with the fisheries staff no long assisting in monitoring the debris trap due to fish transport operations.  Preparations for the adult lamprey passage study were completed on July 28 with the camera installation at entrance weir, SFEW2. Gas bubble trauma examinations continue and results can be requested from the smolt monitoring staff.  The ODFW angling survey for small mouth bass in the project’s tailwater and forebay adjacent to the powerhouse also continues.     

Project:  Ice Harbor

Biologist: Mark Plummer

Biological Technician: Stephen Jeffers
Dates: July 22 - 28, 2011
Turbine Operation
Turbine units 1, 2, 5, and 6 were available for operation this reporting period.  Turbine unit 4 returned to service July 27 at 1842 hours. 

Adult Fish Passage Facilities

Fish facility personnel inspected the adult and juvenile fish passage ways July 25, 26, 27, and 28.
Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.  The current method of monitoring the velocity is channel/tailwater differential, floatation device timing, and visual observation.
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 9.0 feet, off sill with a depth of 8.1 feet, off sill with a depth of 8.3 feet, and off sill with a depth of 8.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 9.5 feet, off sill with a depth of 8.2 feet, off sill with a depth of 8.5 feet, and off sill with a depth of 8.3 feet.  The north shore entrance (NSE) was on sill with a depth of 10.7 feet, on sill with a depth of 10.2 feet, on sill with a depth of 9.7 feet, and on sill with a depth of 9.8 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.   All channel/tailwater differentials were in criteria, except July 25.  On this inspection, the visual north adult fish ladder channel/tailwater elevation was 0.8 feet and the computer indication was 0.96.  This cannot be adjusted as the north adult fish entrance weir lifting mechanism has failed.  The adult entrance weir has fallen to sill at 332.2 fmsl.  Plans are to repair the entrance hoisting mechanism when river flows drop off, allowing access to the entrance weir.   Channel/tailwater differential criteria are 1 – 2 feet.  
Auxiliary Water Supply System:  Normally, 2 of the 3 north shore fish pumps are operated.  North shore fish pump 1 tripped out of service under voltage July 23 at 0605 hours and returned to service at 0626 hours.  All north shore fish pumps were available for operation.  South shore fish pump 1 remains out of service due to vibration issues at the gearbox shaft.  Currently, 6 of 8 south shore fish pumps are operating.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  

STSs/VBSs:  The STS rotations are in continuous run mode as the average length of both the subyearling Chinook and the migratory sockeye is below 120 mm.  No problems were observed on the July STS inspections.  August STS inspections are scheduled for August 15 and 16.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.  
Juvenile Bypass Facility:  The bypass was placed into operation March 23.

Fish Sampling:  Fish sampling for the 2011 season concluded July 7.

Removable Spillway Weir:  The RSW is in operation.   

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	75.1
	59.1
	55.2
	46.8
	65
	64
	4.6
	2.6


*Unit 1 scrollcase temperature.
Other

Inline Cooling Water Strainers:  Cooling water strainer inspections took place in turbine unit 3 on July 5, turbine units 1, 2, 5 and 6 on July 11 and in turbine unit 4 on July 13. The only lamprey mortality found this month was recovered from turbine unit 6.    

Invasive Species: No zebra mussels were observed during this period.

Spill for fish began April 3, 2011.

Project:  Lower Monumental Dam

Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: July 22 - 28, 2011
Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.  Unit 2 was out of service due to loss of GDAC control from July 24 at 1754 hours through July 25 at 0600 hours and remains out service for scheduled annual maintenance.  Unit 5 was out of service on July 24 from 1755 hours to 2242 hours due to a sticky thrust pump mercoid switch.  Unit 6 was out of service on July 25 from 0730 hours to 0945 hours to pull the headgate cylinder. 
Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on July 22, 23, 24, and 27.   

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differential was in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections. 

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 6.9’, 7.0’, 7.4’, and 5.8 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.
SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 7.3’, 7.3’, 7.5’ and 6.4 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Auxiliary Water Supply System: All pumps were in service and operating satisfactorily during this period.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 70.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-30% surface coverage.  No oil was observed in gatewells.
STSs/VBSs:  STS operation remained in continuous run mode as average fork length of sub-yearling Chinook and/or sockeye is less than 120mm.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20 orifices open.  The primary dewatering structure mechanical screen cleaner was returned to service on July 26 at 1300 hours. 

Collection Facility:  No problems occurred this week.  

Transport Summary:  Alternate day transport is occurring with barges arriving on even numbered days in July.  Towboat mechanical problems delayed barge arrival for the July 24 barge until July 25.  Fish were held over the 48 hour holding limit and were loaded at 0630 on July 25 as directed through District Operations.  Fish were released below Bonneville Dam at night during the routinely scheduled release window as usual.   

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	69.8
	54.2
	17.0
	16.6
	65.0
	64.0
	4.0
	3.5


   *Scrollcase temperatures.

Other

Inline Cooling Water Strainers: Cooling water strainers were inspected on July 5.  No live lamprey was recovered.  Mortalities included 23 lamprey, 0 salmon smolts, 0 juvenile steelhead, 0 Siberian prawns, and 11 shad.

Invasive Species: There were no zebra mussels observed at the monitoring stations on July 1. 
Pelican presence at the bypass outfall has been infrequent.  
Project:  Little Goose

Biologist: George Melanson
Dates: July 22 - 28, 2011
Turbine Operation

Turbine units 1 through 5 were available for service throughout the report period.   Turbine unit 6 was removed from service on July 25 for annual maintenance.  All turbine operations were within 1% of best efficiency.  
Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway July 22, 26 and 28.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.0 and 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials measured no differential on all three inspections (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.64 and 2.18 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.10 and 8.38 feet (criteria ≥8.0 ft), NPE weirs were on sill and depths ranged between 5.38 and 5.52 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 5.22 and 5.68 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.3 to 2.0 fps near the SSE.  NSE was not recorded this week due to closure of North shore area.  

Auxiliary Water Supply System:  All fish pumps operated in criteria.  
Juvenile Fish Passage Facility
Forebay Debris/Gatewell Debris/Oil:   Up to 9,000 square feet of woody debris remains in front of the turbine intakes.  Hand removal of debris continued from gatewells.  

Spillway Weir:  The spillway weir was removed from service on July 26 from 0745 to 1530 hours to change from low crest configuration (618 ft) to high crest configuration (622 ft).

ESBS/VBS:   All ESBS operated within criteria this report period.  Underwater camera video inspections of turbine unit 6 ESBSs and VBSs were performed on July 27 from 0840 to 1102 hours.  All screens were determined to be in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated in criteria with 21 to 22 open orifices.  Increased orifices inspections and back-flushing continued.   

Transportation Facility:  Daily collection for this period ranged between 2,638 and 9,051 for a total of 35,808 for the week.  All fish were transported except for mortalities.  Descaling and mortality rates for this report period are 0.15% and 0.68% respectively.

Transport Summary:  Every other day fish loading operations were successfully performed this report period.  However, the towboat developed engine problems following the successful loading of fish on July 24.  The departure was delayed until a towboat mechanic arrived and replaced an engine cylinder head. 
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	88.7
	71.1
	26.3
	21.0
	66.3
	64.4
	5.2
	4.2


*Ladder temperature.
Other

Cooling Water Strainers:  Cooling water strainers on all units were inspected on July 27.  Four juvenile lamprey mortalities were recovered.  

Invasive Species:  The Zebra Mussel substrate monitor was inspected on July 12.  No mussels were observed.  The next inspection is scheduled for August 10. 

Avian Activity: Up to 12 gulls, 18 cormorants and 5 Caspian Terns have been observed in the vicinity of the dam.   
Project:  Lower Granite

Biologists:  Mike Halter and Ches Brooks 

Dates: July 22 - 28, 2011
Turbine Operation

Lower Granite had turbine units 1-5 available for power generation at the beginning of the report week.  Turbine unit 6 is undergoing exciter rehabilitation.  The tentative return to service date for this unit is August 19.  All operating units were run within the 1% guidelines.    

Adult Fish Passage Facility

On July 23, 24, 25, and 27 the Lower Granite COE fisheries biologists performed measured inspections of the adult fishway system.  

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  On July 22 an A-frame and chain hoist system was put in place so that the NSE-1 weir depth can be adjusted relative to the tailwater elevation.  The fish pumps were shut off and the spill pattern adjusted during the approximately six hours this work required.  Head differential readings remained within criteria during all fishway inspections this week. Weir depths at the south shore fishway entrances also remained within criteria on all inspections. Both north powerhouse fishway entrances were on sill during the week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet). Weir depths at the north powerhouse entrances ranged from 5.3 to 5.7 feet.  Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 4.9 and 5.4 feet on both gates (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.86 to 1.02 feet per second and averaged 0.95 feet per second.

Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and two were run all week, except as noted above, the pumps were shut down on July 22 from 0934 hours to 1539 hours to allow the work on NSE-1.
Juvenile Fish Passage Facility

The juvenile fish facility sample rate was increased from 10% to 20% at 0700 hours on July 28.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed. 

ESBSs/VBSs:  The last VBS/ESBS video inspections were attempted on June 24-25.  They were cancelled due to near zero water visibility and concerns with the increased spill levels (due to the need to shut off units one at a time) increasing dissolved gas levels.  The next inspections have been moved up to August 5-7.  

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Vegetative debris levels (mainly Elodea) dropped off significantly this report week.  On occasions of partial clogs the separator technicians were able to clear the inclined screen with the power air rake tool that the maintenance staff developed. It was not necessary to go into bypass mode to clean the inclined screen during this report period. 

Transportation Facility:  The fish transportation facility operated well during the week.  Raceways were swept prior to barge loading and a moderate amount of vegetative and woody debris was removed.  The facility has continued utilizing the larger (lamprey friendly) mesh raceway tailscreens.   

Transport Summary:   Every other day fish barging operations proceeded according to schedule on the even numbered days of the report week.  Operations went smoothly all week.  

Removable Spillway Weir:  The RSW operated normally as part of the spill plan.  

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	71.6
	54.8
	18.9
	18.4
	67.6
	65.5
	5.0
	4.2


*Scrollcase temperature

Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected for lamprey entrainment on July 28.  A total of 41 lamprey were found in the strainers over a combined run time of 3235.5 unit hours.  Unit 6 is out of service and was not inspected.    
Invasive Species:  The zebra mussel traps near the adult fishway exit were examined for zebra mussels on the July 11 inspection.  No evidence of zebra mussels was found.

Research:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All wild steelhead and Chinook captured are being PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead or Chinook (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.  Scale samples are also being taken from one out of every three hatchery Chinook.  Sort by code Lemhi origin Chinook are being radio-tagged and scale and genetic samples taken. 

