U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#15-2012
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: June 8 - 14, 2012
Turbine Operation

McNary had 12 to 13 units available for power generation this week.  Unit outages are recorded in Table 1.    

Table 1.  Unit Outages at McNary Dam.

	Units
	Outage Dates
	Outage Length
	Reason

	3
	Jun 4 to Jan 30.
	8 months.
	Rewind contract.

	8
	Jun 11 to Jan 30.
	8 months.
	Rewind contract.


No turbine units operated outside the 1% hard constraint efficiency criteria this week.  On June 9, unit electrical loads were reduced to a 44 to 50 megawatts operating range in support of wind generation.             

Adult Fish Passage Facilities

On June 8, 10 and 13, the McNary fisheries biologist performed measured inspections of the adult fishways.  Visual fish counts continued.    

On June 15, facility personnel will begin to monitor ladder exit water temperatures.  Also that day, entrance weirs SFEW1, NFEW2 and NFEW3 will be lowered nightly from 2100 to 0400 hours in support of lamprey passage.  SFEW2 will not be lowered this year as lamprey passage stilts were previously installed on the weir.  Weir programming will be altered to reflect this change. 
Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections, except on June 10 when the Washington ladder head over weir differential measured 0.8 feet.  The Washington ladder also experienced multiple weir alarms.   Normal operation resumed after the operators reset the alarms and adjusted the set points.  On June 13, the regulating weir triggered an alarmed and was reset.  Again, the operators adjusted the set points.    

At the Oregon exit, the south traveling screen also experienced multiple alarms which the operators reset.  Screen differential monitoring efforts revealed no problems.  On June 13, a biologist found the north traveling screen in bypass mode.  The operators returned it to automatic operation.        

Fishway Entrances and Collection Channel:  Spill turbulence and hydraulic gradients make it difficult for the project to maintain entrance weir depth and calibration.  Electricians calibrated all entrance weirs from June 11 to 13.  The weirs were placed in manual mode during the calibration work.     

On the Washington ladder, the biologist found all inspection points in criteria.  Most Oregon inspection points were in criteria.  All week, the south powerhouse entrance, SFEW1, measured depths ranging from 7.8 to 8.2 feet.  On June 8 and 13, SFEW2 measured depths of 7.5 and 8.7 feet, respectively.  These readings are due to hydraulic gradients.  It is also possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.0 to 1.1 feet.  On June 13, the north powerhouse entrance, NFEW3 measured a depth of 8.9 feet.  Collection channel velocities averaged 1.8 feet per second.  The new velocity meter has been functioning well.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile facility continues to provide the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no interruptions in service.                    

Juvenile Fish Passage Facility

The spring bypass season continues with alternating days of primary and secondary bypass operations.  The switch between the 2 bypass modes takes place every morning at 0700 hours.  No deviation from this schedule occurred.  This week, 42,229 smolts and 3,950 juvenile lamprey were touted through the secondary bypass.    

Forebay Debris/Gatewell Debris/Oil:  Forebay debris accumulations were light or very light this week.  Most of the debris has accumulated along the powerhouse.  Debris distribution is mainly affected by spillway and turbine operations and weather.  Trash rack differentials were satisfactory this week and no problems were seen.  The fisheries staff observed no problems in the gatewell slots. 

ESBSs/VBSs:  ESBSs have been deployed in all turbine units.  No ESBS camera inspections occurred this week due to fish salvage operations in turbine unit 8.  The screen in 7C slot triggered an alarm on June 13.  The operators subsequently switched the ESBS cleaning brush operation to transducer bypass mode.              

The fisheries staff continued to monitor VBS differentials and no screens were found out of criteria.  However, on June 8, 13 and 14, as a preventative measure, project personnel cleaned a total of 13 VBSs.  VBS rehabilitations are now in progress.     

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in use and no blockages were observed.  Mechanics installed three new orifice operators during this report period.  All systems operated well in automatic mode.  The transition screen cleaner will remain out of service until a channel shutdown takes place.  Fisheries personnel continue to monitor the collection channel during all shifts when in primary bypass mode and during VBS cleaning operations.  Electricians continued to rewire lighting in the channel to improve night observations.   

Transportation Facility:  During the spring bypass season, both bypass modes return all fish to the river.  PIT tag detection occurs in the full flow pipe during primary bypass operations and throughout the facility during secondary bypass operations.  Smolt monitoring occurs only during secondary bypass operations. The primary (A and B) PIT tag slide gates remained off and closed, as the return to river lines provide a better bypass route for PIT tagged fish.  The system received scheduled maintenance this week.  The secondary (C and D) PIT/bypass gates were off and open.  The fisheries staff turns the sample gates off or on at 0700 hours each day so the gates will be functional during secondary bypass operations.

Last week, the air conditioning unit above the PIT tag room began to leak into the room.  Parts are on order and the fisheries mechanics are collecting the water and monitoring the leak.  Other maintenance in progress include the replacement of the oil reservoir at raceway 4 (part of raceway release system), and continued work on safety ladders for the east raceways.  Ice block checks of the return to river lines revealed no blockages.  However, due to the new location of the bypass outfall and high tailwater elevations, the fisheries staff is having difficulty seeing the ice blocks exit the pipe.   

Transport Summary:  There is no fish transport in progress at this time. 

River Conditions

River conditions during the week are outlined in Table 2 which summarizes data provided by the smolt monitoring staff.  The data day is from 0700 to 0700 hours.  The spring and summer spill programs call for 40 and 50 percent of flow being spilled, respectively.  The summer spill program began on June 12 at 1200 hours.  Due to high flows, 52 to 58 percent of total river flow was spilled this week.

As recorded in the control room log, spill bay 19 was closed from June 7 at 0730 hours (previous report period) to June 8 for spill bay weir removal, the installation of a standard gate, followed by the attachment of the standard gate to a spill hoist.  On June 7, from 1435 to 1611 hours, bay 20 was closed.  The project reopened the bay with the TSW still in place.  From June 8 at 0712 hours to June 9 at 1203 hours, bay 20 was closed for spill bay weir removal, standard spill gate installation followed by gate attachment to spillway crane number 6.  

On June 15, the smolt monitoring staff will begin routine water temperature monitoring across the project. 

Table 2.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	365.6
	327.9
	204.0
	178.2
	56.7
	54.9
	5.6
	     4.0


*Control room data.
Other

Inline Cooling Water Strainers:  Main unit cooling water strainers were examined June 5.  A total of 25 juvenile lamprey were recovered.  All were mortalities with the exception of 1 lamprey which was recovered live from turbine unit 1.  Three unidentifiable smolt mortalities were also recovered from turbine unit 1.  The next series of cooling water strainer examinations will occur in early July.  

Invasive Species:  next zebra mussel trap examination will occur in mid-June.         
Avian Activity:  APHIS continued hazing efforts and Corps day shift technicians continued to conduct bird counts.  Tailrace high counts (exclusive of the bypass outfall) included 9 gulls, 9 terns, 8 cormorants and 11 pelicans.  Most of these are feeding in the spill area.  Pelicans are feeding on shad along the navigation lock wall.   Cormorants were regularly roosting on the navigation lock wall.  Occasionally terns and pelicans pass over the powerhouse flow.  Pelicans in this vicintiuy may be foraging for adult shad along the Oregon Shore.  Bypass outfall high counts included 5 gulls, terns, 3 pelicans and 1 cormorant.  Forebay high counts included 5 grebes, 3 terns, 1 pelican with an occasional osprey, cormorant or tern.  Hazing efforts appear to be working well on grebes.  Fifty pelicans were observed on the rocks by the Washington shore boat dock.  These pelicans may be foraging for adult shad along the powerhouse pier noses.  Three grebes entered the gatewell slots this week.  The general maintenance crew removed all three.  The other 2 grebes reported last week passed into the collection channel and out of the system.  The bypass outfall water cannon remained out of service.  District personnel are investigating the possible installation of a second pump to restore service later this month.  This pump would be used until the original pump can be repaired.  APHIS continued hazing activities with two 8 hour shifts, which covers the 16 hours of day light typical this time of year.  The propane hazing cannons are operating well though strong winds do interrupt their operation.  Next week, project personnel will place three new cannons into service and return the ones borrowed from the Ice Harbor Operating Project.        

Research: Current onsite research includes the juvenile salmonid passage study, Gas Bubble Trauma (GBT) examinations, the adult lamprey passage study and ODFW angling efforts to sample Northern Pikeminnow and other fish species that prey on smolts.  Another contractor has delayed the Oregon exit traveling screen study.  On June 14, NOAA fisheries researchers sampled smolts for their non-native predatory diet analysis study.

Fish Salvage:  Project personnel conducted a fish salvage operation in turbine unit 8 on June 12.  Although no fish were found in the scroll case, 5 channel catfish were recovered from the draft tube, 1 of which was lost.  These were the only fish observed.

Project:  Ice Harbor

Biologist:  Mark Plummer 

Biological Technician:  Stephen Jeffers
Dates: June 8 - 14, 2012
Turbine Operation
Turbine units 1 – 6 were available for operation this reporting period.  Turbine unit 6 was out of service June 11 from 1030 hours to 1215 hours due to governor work.  

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fish passage ways June 12, 13, and 14. 
Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. Channel/tailwater differential criterion is 1 – 2 feet.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.5 feet, off sill with a depth of 8.1 feet, and off sill with a depth of 8.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 7.2 feet, off sill with a depth of 8.5 feet, and off sill with a depth of 10.8 feet.  The north shore entrance (NSE) was off sill with a depth of 8.3 feet, off sill with a depth of 10.3 feet, and off sill with a depth of 9.5 feet.  The NSE and NFE are currently being operated in manual mode due to tailwater fluctuations caused by spill.   On the June 12 NFE inspection, the out of criteria entrance weir depth was reported to the shift operator for adjustment.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  Channel velocities readings ranged from 1.4 fps – 1.9 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  All 8 south shore fish pumps were operated.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactory.  

STSs/VBSs:  The STSs are in continuous run mode due to the size of juvenile fish less than 120 mm at Lower Monumental Fish Facility as per FPP.  June inspections are scheduled for June 19 and 20.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was placed in service on March 19. Twenty orifices are open.  No problems to report.    
Juvenile Bypass Facility:  The bypass was put into operation March 19.

Fish Sampling:  Juvenile fish sampling occurs Monday and Thursdays.

June 11:

	Species
	Sampled
	#Descaled
	Morts
	Avian Marks

	
	
	
	
	 

	C-CH
	1
	0
	0
	0

	UC-CH
	3
	0
	0
	0

	C-CH-O
	38
	1
	0
	0

	UC-CH-O
	42
	0
	0
	0

	C-SH
	16
	1
	0
	0

	UC-SH
	5
	0
	0
	1

	C-COHO
	---
	---
	---
	---

	UC-COHO
	---
	---
	---
	---

	C-SOCK
	---
	---
	---
	---

	UC-SOCK
	---
	---
	---
	---

	
	 
	 
	 
	 

	TOTAL
	105
	2
	0
	1


June 14:

	Species
	Sampled
	#Descaled
	Morts
	Avian Marks

	
	
	
	
	 

	C-CH
	---
	---
	---
	---

	UC-CH
	4
	0
	0
	0

	C-CH-O
	31
	0
	0
	0

	UC-CH-O
	54
	1
	0
	0

	C-SH
	7
	1
	0
	2

	UC-SH
	4
	0
	0
	1

	C-COHO
	---
	---
	---
	---

	UC-COHO
	1
	0
	0
	0

	C-SOCK
	---
	---
	---
	---

	UC-SOCK
	---
	---
	---
	---

	
	 
	 
	 
	 

	TOTAL
	101
	2
	0
	3


Removable Spillway Weir:  The RSW is in operation.  Spill for fish began April 3, 2012.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	101.7
	81.3
	81.7
	49.1
	56
	56
	3.9
	3.4


*Unit 1 scrollcase temperature.
Other

Inline Cooling Water Strainers: Main turbine cooling water strainer inspections are scheduled for June 19 and 20.

Invasive Species: No zebra mussels were observed during inspections.

Project:  Lower Monumental
Biologists: Bill Spurgeon and Elizabeth Lindsey
Dates: June 8 - 14, 2012
Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.  Unit 3 was out of service to re-plumb the governor oil filter piping from 1159 to 1635 hours on June 11.  Unit 4 was out of service to raise the intake gate for inspection from 1231 to 1515 hours on June 13.
Adult Fish Passage Facility

The adult fishway was inspected by Corps and State biologists on June 8, 9, 10, 11, 13, and 14.   

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  

Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.
SPE 1 and SPE 2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 7.2’, 7.7’, 7.6’, and 6.9 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 6.8’ and 6.6’ feet. SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

The collection channel velocity remained in criteria (1.5 - 4.0 ft/sec) this week. 

Auxiliary Water Supply System:  All AWS pumps were in service and operating during this period. 
Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 10.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-15% surface coverage.  

STSs/VBSs:  STS operation remains in continuous run mode due to sockeye and Chinook under 120 mm in the sample.
Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20-21 orifices open.

Collection Facility:  The facility is in collection for transport mode.  Battelle research on fish passage and survival continued this week.  
Transport Summary:  Every-other-day transport is occurring with barges departing on odd numbered days.  
River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	99.1
	78.7
	60.8
	25.9
	55.5
	54.0
	4.0
	2.8


*Scrollcase temperatures.

Other

Spring spill operation was initiated at 0001 hours on April 3.  

Inline Cooling Water Strainers: Cooling water strainers were inspected on June 4.  No live lamprey were recovered.  Mortalities included 2 juvenile lampreys, 5 juvenile salmon, and 1 Siberian prawn.  About 3 dozen decomposed juvenile lampreys were removed from units 2 and 4 cooling water strainers.   

Invasive Species: There were no zebra mussels observed at the monitoring stations on June 1.

Avian Activity: Piscivorous bird numbers were very low this week.  Cormorants and terns were the prominent species observed.  Hazing ended on June 2. 

Project:  Little Goose

Biologist: Richard Weis
Dates: June 8 - 14, 2012
Turbine Operation

Turbine units 1-6 were available for service throughout this report period.  All turbine units were operated within the 1% efficiency criteria.

Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway June 8, 11 and 12.
Fish Ladder: The ladder exit head differentials ranged between 0 and 0.1feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.1 and 1.3 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials ranged between 0 and 0.1feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorally.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.6 and 2.2 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.3 and 8.4 feet (criteria ≥8.0 ft). NPE weirs rested on sill and depths ranged between 5.4 and 6.0 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 5.3 and 6.5 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.6 to 2.3 fps near the SSE. 

Auxiliary Water Supply System:  All fish pumps operated within criteria this report period. All three pumps were removed from service on June 8 from 1200 to 1220 to pull new wiring for the fish pumps.

Juvenile Fish Passage Facility
Forebay Debris/Gatewell Debris/Oil:  Surface woody debris measured up to 300 square feet inside the trash shear boom. Trash racks on unit 1and 2 were raked on June 14 and 20 yards of debris were removed. Units 3-6 were done on June 13 with 30 yards removed.
Spillway Weir:  The spillway weir operated in the high crest position.  

ESBS/VBS:  All ESBS operated within criteria this report period.  Drawdown measurements across ESBS and VBS were done on June 14 on units 2-6.  All measurements indicated no debris buildup and screens in good operating criteria.    

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 22 open orifices.

Transportation Facility:  The facility continued collection for transport.  Daily estimated collection ranged between 11,201 and 26,651. The estimate collection for the week totaled 144,581.  All fish were transported except for 3 fry that was returned to the river for additional growth.  Descaling and mortality rate for the period was 1.0% and less than 0.1% respectively.
Transport Summary:  All barging operations were satisfactorily completed. 
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	95.1
	82.2
	52.6
	30.0
	55.0
	53.3
	3.2
	2.5


*Ladder temperature.

Other

Inline Cooling Water Strainers:  On June 12, all cooling water strainers were inspected.  4 Juvenile Lamprey and 2 unidentified smolts were removed.  All were mortalities.

Invasive Species:  The zebra mussel substrate monitor was inspected on June 6.  No mussels were observed.  The next inspection is scheduled for July 6.

Avian Activity: Bird hazing by USDA continued this week.  Piscivorous birds observed during any single surveying event included 3 seagulls, 13 cormorants, 2 Terns and 2 pelicans in the vicinity of the dam.     
Project:  Lower Granite

Biologist(s):  Mike Halter and Ches Brooks 

Dates: June 8 - 14, 2012
Turbine Operation

Lower Granite had turbine units 1, 2, 3, 5 and 6 available for power generation at the beginning of the report period.  Turbine unit 4 is out of service for cavitation repair.  All turbine units (except unit 1) were operated within the 1% operation criteria.  Unit 1 turbine blades have been welded at a fixed angle and cannot achieve the 1% criteria.  This issue will be addressed after the spring freshet.            

Adult Fish Passage Facility

On June 8, 10, and 14 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system. 

Fish Ladder:   All criteria were met during this week’s inspections.   

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections, with the exception of the June 14 inspection when the north shore entrance was under criteria at 0.8 feet (criterion 1.0 – 2.0 feet).  Weir depths at the south shore fishway entrances also met criteria during all weekly inspections.  The north powerhouse fishway entrances were on sill on all inspections this week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 4.5 to 5.6 feet.  Weir depths at the north shore entrances ranged from 4.5 to 6.8 feet on the weekly inspections.  North shore weir depths are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.93 to 1.11 feet per second and averaged 1.0 feet per second during the weekly inspections.
Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and two satisfactorily operated all week.    
Juvenile Fish Passage Facility

The last daily barge departed Lower Granite on May 28.  Every other day barge operations began on May 30 and fish barges will depart Lower Granite on the odd numbered days of the month during June.  The sample rate was increased from 2% to 4% at 0700 hours on June 12 and remained at that level for the remainder of the report week.    

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.   

ESBSs/VBSs:  There were no problems with fish screens reported during the week.  ESBS video inspections were last attempted on May 19, but were cancelled due to low water clarity and some camera problems.  The camera has been repaired and the next inspections are scheduled for mid June.       

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels lightened somewhat during the week.  It was not necessary to go into bypass mode to clean the inclined screen during this report period. 

 Transportation Facility:  The JFF operated smoothly during the week.  Avian hazing activities continued on a 16 hour/day basis and prevented the buildup of gulls and other avian predators.   

Juvenile lamprey recently began to be noted in the raceways.  Lamprey friendly tail screens (with larger mesh openings) were deployed in all raceways on June 10.
Transport Summary:  The first every other day barge left Lower Granite on May 30.  The final research barge of the season (index barging) departed Lower Granite on April 26.  Research fish are now being barged along with the general fish collection.  Fish barging operations have been progressing smoothly.   

Removable Spillway Weir:  Mandatory spill operations began at 0000 hours on April 3. The RSW continues to be operated in support of general spill operations. 

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	102.1
	81.0
	56.9
	29.4
	56.0
	53.7
	3.6
	2.8


*Scrollcase temperature.
Other

Visual adult fish counting at the adult ladder is taking place between the hours of 0400 and 2000 hours.  Visual fish counting began on April 1 and is scheduled to continue through October 31.
Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on May 31.  A total of 32 lamprey were found in the strainers over a combined run time of 3,389.9 unit hours.  The next cooling water strainer inspections are scheduled for late June.
Invasive Species:  The zebra mussel trap near the adult fishway exit was last examined June 7.  No evidence of zebra mussels was found.
Research
 Adult Fish Trap Operations:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes. 
 Idaho Fish and Game (IDFG) Genetic Stock Identification:  The goal of this study is to develop fine-scale genetic profiles for natural origin salmon and steelhead; develop genetic stock identification (GSI) techniques to estimate stock-specific escapement over LGR, monitor abundance, productivity and distribution of naturally produced adult and juvenile steelhead and salmon; research and monitor stock-specific life history characteristics. At LGR the goal of the study will be to enumerate and characterize the natural production of spring/summer Chinook salmon and steelhead above LGR with regards to age composition and genetic stock profiles. IDFG will sample every day until the first part of July with the goal to collect between 2,000-5,000 genetic samples each from yearling spring/summer Chinook and steelhead and 500-3,000 genetic samples from subyearling fall Chinook.
Nez Perce Tribal Fisheries Steelhead Kelt Research: The Nez Perce Tribal Fisheries in coordination with the Corps and The University of Idaho started steelhead kelt research work for the season this week at the holding tanks upstream of the main fish facility.   Clipped and unclipped kelts are being examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts will be blood sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river.  

NOAA-Fisheries Transport Study:  NOAA staff PIT-tagged migrating smolts at the fish facility upstream raceways for their Transport Evaluation Study, in order to compare smolt to adult returns of in-river migrating smolts to the smolt to adult returns of transported smolts.  This week 1,230 clipped yearling Chinook, 325 unclipped yearling Chinook, 15,998 clipped subyearling Chinook, 19,687 unclipped subyearling Chinook, 4,153 clipped steelhead, 340 unclipped steelhead, 3 clipped sockeye, 53 unclipped sockeye and 363 coho were collectively, marked and transported or handled and transported.   

NOAA-Fisheries Reach Survival Study:  NOAA staff PIT-tagged smolts for their Survival Study to evaluate the in-river survival of juvenile salmonids bypassed into the tailrace at Lower Granite.  This week 370 clipped steelhead and 248 unclipped steelhead were PIT-tagged and bypassed to the tailrace.
