U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#29-2012
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: September 14 - 20, 2012
Turbine Operation

McNary had 8 to 9 units available for power generation this week.  All available units operated within the 1% efficiency criteria.   Unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

	Units
	Outage Dates
	Outage Length
	Reason

	3
	Jun 4 to Jan 30.
	8 months. 
	Rewind contract.

	8
	Jun 11 to Jan 30.
	8 months.
	 Rewind contract.

	11 and 12
	Sep 3 to Oct 25.
	3 months.
	Install digital relay.

	4
	Sep 10 to 20.
	10 days.
	Annual maintenance.

	14
	Sep 15 to Sep 17 and Sep 18 to unknown.
	2 days 
and unknown.
	High turbine bearing temperature.

	6
	Sep 18.
	3.3 hours.
	DC ground.

	5, 6 and 7
	Sep 18.
	50 minutes total.
	ESBS camera inspections.


Adult Fish Passage Facilities

On September 14, 17 and 19, the McNary fisheries biologist performed measured inspections of the adult fishways.  NOAA fisheries staff conducted their monthly inspection on September 20.  On September 17, ladder exit temperature monitoring concluded for the season.    

Visual fish counts continued, as did video adult lamprey counts and the nightly lowering of entrance weirs SFEW1, SFEW2, NFEW2 and NFEW3.  Video adult lamprey counts and the nightly lowering of entrance weirs will conclude for the season on September 30.  The cameras at SFEW1 and SFEW2 were removed earlier this week.        

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  The window cleaning brush at the Washington ladder count window cleaning jammed at the bottom of the slot twice this week.  In each case, project personnel were able to resolve this issue.   Debris loads along the north shore remained low.  At the Oregon exit, screen differential monitoring results were satisfactory.  Woody debris along the Oregon shore remains light and scattered with location dependant on wind direction.
Fishway Entrances and Collection Channel:  Since the end of routine spill for fish passage, the project has been able to maintain entrance weir depth and calibration more consistently.     

All Washington ladder inspection points met criteria this week as did most Oregon ladder inspection points.  All week, the south powerhouse entrance weir, SFEW2, measured depths ranging from 8.7 to 8.8 feet.  On September 14 and 19, SFEW1 respectively measured depths of 8.5 and 8.4 feet.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.1 to 1.2 feet.  On September 14, both north powerhouse entrances NFEW2 and NFEW3 measured weir depths of 8.9 feet.  These weir depths are typical this time of year due to low tailwater elevations.  All other Oregon inspection points were in criteria.   

Collection channel velocities averaged 1.3 feet per second.  The permanently mounted velocity meter remains out of the water due to a shortened cable.  Until this can be resolved, surface velocity measurements will be taken manually. 

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile fish facility continues to provide the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no interruptions in service this week.                        

Juvenile Fish Passage Facility

Truck transport proceeded smoothly with no interruptions in fish collection.  For the week, 12,215 smolts were collected for transport.  In addition, 270 juvenile lamprey and 17,825 juvenile shad were collected.  Collection for the transport season will conclude at 0001 hours on October 1.   

Forebay Debris/Gatewell Debris/Oil:  Forebay debris ranged from very light to light this week.  Debris location is mainly affected by wind and project operations.  The fisheries staff continued monitoring trash rack differentials with satisfactory results.  No racks were cleaned this week.  Gatewell observations revealed no problems       

ESBSs/VBSs:  ESBSs are deployed in all turbine units except unit 3 which is out of service until January 2013.  ESBSs in slots 1A and 7C remain in transducer bypass mode.  Operators reset ESBS cleaning brush travel distances in slots 1B, 1C and 13C after a biologist noted that the brushes were not traveling to the end of the screens.  Video-camera ESBS inspections took place in turbine units 5, 6 and 7 this week.  All inspected screens were found in satisfactory condition.  The fish facility staff continued to monitor VBS differentials, finding 5 screens out of criteria.  On September 14, 17 and 20, project personnel cleaned these screens plus 14 others as a precautionary measure.  Due to bryozoan (sponges) growth, maintenance crews are now cleaning both sides of the VBSs at times.

VBS rehabilitations continued with the September 10 removal of the screen in slot 3B.  As mentioned above, turbine unit 3 is to remain out of service until January 2013.  On September 20, a newly rehabilitated screen (originally taken from slot 3A) replaced the VBS in slot 13A. The VBS in slot 3C was cleaned and removed September 19 for rehabilitation, leaving all unit 3 VBS slots vacant.  These slots will be used as a staging area for swapping VBSs as they are rehabilitated.  

On September 16, the VBS differential in slot 1A slot measured 1.6 feet.  The operator “burped” the unit by taking it out of and into service.  After the “burp”, the differential measured 1.1 feet and the VBS was cleaned the next day.  

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in use with no blockages observed.  Biologists opened and closed orifices associated with units 3 and 8 as needed in support of VBS rehabilitation efforts (these units are out of service).  When orifices in units 3 and/or 8 were closed, additional spare orifices were opened or closed in units 11 and 12 as needed to maintain collection channel elevations.  
On September 15, a biologist turned a backup air compressor off, after noting the compressor ran continuously.  The backup compressor is used to supply air to the rectangular screen air bubbler.  The maintenance staff later determined that the compressor required a switch replacement.  Until then, the compressor will remain off as the powerhouse air supply has been very reliable.  
The transition screen cleaner remains out of service until a channel shutdown occur; otherwise all systems operated well in automatic mode (other than the compressor).  The fisheries staff continued to monitor the channel during day shifts during VBS cleaning and during forebay debris removal operations.

Transportation Facility:  Collection for truck transport continued.  During collection, PIT tag detection occurred in the full flow bypass pipe and throughout the facility.  The primary (A and B) PIT tag slide gates remained in service and the secondary (C and D) PIT/bypass gates remained closed (and off) to facilitate the routing of fish to the raceways.  Water balloons were used to check for debris blockages within the PIT tag system.  No blockages were found.  The PIT tag system did undergo some minor maintenance this week.  

Smolt monitoring occurred daily and sample gates remained on during collection.  When sample rates exceed 20 percent of the collection, the PIT tag system is placed in override mode.  This mode of operation allows the PIT tag gates to function when the sample gates are open.  When not in override mode, PIT tag gates do not function when the sample gates are open.     

On September 15, a biologist noted the raceway gantry “stalling” when in use.  Although this development does not preclude the use of the gantry, this situation will be monitored.  

Transport Summary:  Every other day trucking continues.  Trips were successfully completed on September 15, 17 and 19 without incident.    

River Conditions

River conditions during the week are outlined in Table 2 using data provided by the smolt monitoring staff.  The data day is from 0700 to 0700 hours.  All spill recorded was in excess of powerhouse capacity.  Spill occurred on five data days.               

Table 2.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	126.2
	97.8
	22.2
	0.0
	66.1
	65.7
	6.0
	     6.0


*Control room data.
Other
Inline Cooling Water Strainers:  Project personnel conducted main unit cooling water strainer examinations on September 17.  No juvenile lamprey were recovered although 3 smolts mortalities were retrieved from unit 1.   Most of the fish recovered were juvenile shad.  Units 3 and 8 are out of service until January, 2013.  The next cooling water strainer examination will occur in early October.    
Invasive Species:  The next zebra mussel trap examination will occur on September 23.

Avian Activity:  Corps technicians continued bird counts.  Tailwater high counts (exclusive of the bypass outfall) included 42 terns, 12 gulls and 3 cormorants.  Most of these were seen in in the vicinity of the powerhouse.  The terns and gulls were observed only on a single day.  No birds were seen at the bypass outfall.  High forebay counts included 2 gulls and an occasional osprey, grebe or cormorant.  Most of these birds are assumed to be feeding on shad.  No grebes were observed anywhere else on project.  Gulls and cormorants continue to roost on the rocks by Washington shore boat dock.  APHIS hazing activity concluded August 4.  Bird counts are slated to end September 30.
The bypass outfall water cannon remained out of service.  Current plans are to install a second pump and complete walkway grating repairs in late September.  The propane hazing cannons continued to operate well.  
Research:  The adult lamprey study is now the only current onsite research in progress.  This work is taking place only at the ladder exits.  Contractors began removing juvenile passage study equipment this week.  
On September 27, district personnel will remove video cameras at the entrance and exit of the 80’ adult fallback return line between the separator and the recently constructed bypass outfall pipe.  This monitoring equipment was installed in response to NOAA Fisheries concerns regarding the potential for passage delays or injuries inside the return line.      

Project:  Ice Harbor

Biologist:  Mark Plummer 

Biological Technician:  Stephen Jeffers
Dates: September 14 - 20, 2012
Turbine Operation
Turbine units 1-3 were available for operation this reporting period.  Turbine units 4-6 remain unwatered and out of service.   

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fish passage ways September 17, 18, 19, and 20.
Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.8 feet, off sill with a depth of 7.0 feet, off sill with a depth of 7.9 feet, and on sill with a depth of 7.9 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 7.9 feet, on sill with a depth of 7.2 feet, off sill with a depth of 8.8 feet, and on sill with a depth of 8.6 feet.  The north shore entrance (NSE) was on sill with a depth of 8.4 feet, on sill with a depth of 7.6 feet, off sill with a depth of 8.8 feet, and on sill with a depth of 8.0 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  Channel/tailwater differential criterion is 1 – 2 feet.  All out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings ranged from 2.6 fps – 3.0 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without any problems.  Seven of the 8 south shore fish pumps operated satisfactorily.  On September 20, south shore fish pump 6 was turned on at 0747 hours and south shore fish pump 4 was placed out of service at 0906 hours due to excessive gearbox oil leakage.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  

STSs/VBSs:  The STS screens are in cycle-run mode.  No problems were found during the September 4 STS inspections of units 4, 5, and 6.  September inspections for units 1, 2, and 3 are tentatively scheduled for September 24 and 26.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was placed into operation March 19.  Twenty orifices are open.  No problems to report.    
Juvenile Bypass Facility:  The bypass was placed into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill for fish ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	29.3
	17.1
	0.0
	0.0
	67
	66
	7.4
	7.2


*Unit 1 scrollcase temperature.
Other

Inline Cooling Water Strainers:  Cooling water strainer inspections are scheduled to take place September 24. 

Invasive Species:  No zebra mussels were observed during adult fishway inspections.  

Project:  Lower Monumental
Biologists: Bill Spurgeon and Elizabeth Lindsey
Dates: September 14 - 20, 2012
Turbine Operation

The units are being operated within the hard constraint 1% operational criteria.  Unit 4 was removed from service at 0945 hours on August 13 for six year annual maintenance and remained out of service through this period.  
Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC/State biologists on September 15, 16, 19, and 20.   

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) during all inspections.  

Fishway Entrances and Collection Channel:  NSE1 and NSE 2 weir gates were within depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) during all inspections.  While on sill the gate depth readings were 6.3’, 6.9’, 6.2’, and 5.6 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 7.2’, 7.2, and 6.5 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Collection channel velocities remained in criteria (1.5 - 4.0 ft/sec). 

Auxiliary Water Supply System: All AWS pumps were in service and operating during this report period. 

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 20.5 square yards of forebay debris observed during this report period.  Gatewell debris ranged from 0-14% surface coverage.   No oil was observed in the gatewells this week. 

STSs/VBSs:  STS operations remain in cycle-run mode.  STSs were inspected on September 4, 5 and 6.   A row of loose clips was observed on the STS in gatewell slot 2B on September 4.  The screen was repaired as a preventative measure on September 5.    
Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.  The primary dewaterer automatic weirs remain set at 528.1 feet to eliminate sudden water level fluctuations in the separator.    

Collection Facility:  The facility is in collection for transport mode.  Facility mortality exceeded 6% on every day this week.  Percent mortality was 22.4, 34.8, 46.9, 31.4, 27.3, 14.1, 23.4, and 26.5, respectively.  The average facility mortality rate this week was 26.5% (97 mortalities out of 366 juvenile salmonids collected).  Sampled sub-yearling Chinook had an average columnaris rate of 14.2% (40 infected out of 282 sampled).  As is facility standard procedure, each transport tank is treated with salt to ease fungal and bacterial infection.  No other problems occurred.  
Transport Summary:  Alternate day midi-tanker transport is occurring with trucks departing on odd numbered days. 
River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	28.5
	18.6
	0.0
	0.0
	66.0
	65.0
	5.0+
	4.6


*Scrollcase temperatures.

Other

Summer spill operation ended at 0001 hours on September 1.  

Inline Cooling Water Strainers:  Cooling water strainers were inspected on September 17.  No lamprey were recovered.   Mortalities included 1 juvenile carp, 2 juvenile channel catfish, 3 Siberian prawns, 5 juvenile shad, and 1 undetermined species. 
Invasive Species: No zebra mussels were observed at the monitoring stations on September 3.
Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls and cormorants were the prominent species observed.  Hazing ended on June 2. 
Project:  Little Goose

Biologist: Richard Weis
Dates: September 14 - 20, 2012
Turbine Operation

Turbine units 1, 2, and 5 were available for service for this report period.  Turbine units 3, 4 and 6 remained out of service for annual maintenance and exciter replacement.  All turbine units were operated within the 1% efficiency criteria.

Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on September 14, 18 and 20.
Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs remained steady at 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials remained steady at 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.2 and 2.0 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.1 and 8.3 feet (criteria ≥8.0 ft).  NPE weirs rested on sill and depths ranged between 5.0 and 6.2 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 6.2 and 6.3 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.2 to 1.6 fps near the SSE and 2.0 to 2.6 fps near the NSE.   On September 6, collection channel subsurface water velocity measured 2.56 fps (criteria 1.5 to 4.0) near the NPE.

Auxiliary Water Supply System:   All fish pumps operated within criteria this report period.
Juvenile Fish Passage Facility
Forebay Debris/Gatewell Debris/Oil:  Up to 400 square feet of debris in front of the spillway by the end of this report period.    

Spillway Weir:  The spillway weir was not in service during this report period.  Summer spill for fish passage ended on September 1.

ESBS/VBS:  Drawdown measurements across ESBS/VBS associated with turbine unit 1 and 2 was performed on September 19.  All measurements indicated no debris buildup.  The ESBS screen in slot 2A was found with a trouble light on and was reported to the operator on September 19.  The limits were subsequently adjusted and the brush resumed normal operation.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 18 open orifices.

Transportation Facility:  The facility continued collection for transport.  The facility is operating at 100% sample rates.  Daily smolt collection ranged between 3 and 13 and totaled 45 for the week.  Descaling and mortality rate for the period was 0% and 2.2% respectively.  

Transport Summary:  Due to low numbers of fish collected, Lower Granite continued transporting Little Goose Fish during this period.  Salt in small concentrations of approximately 1 g/L is added to the midi-tank water to treat Columnaris disease and reduce stress.  All trucking operations were satisfactorily completed.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	24.2
	20.7
	0
	0
	65.6
	65.2
	6+
	6.0


*Ladder temperature.

Other

Inline Cooling Water Strainers:  All cooling water strainers were inspected on September 19.  No fish were observed.   

Invasive Species:  The Zebra Mussel substrate monitor was inspected on September 06.  No mussels were observed.  The next inspection is scheduled for October 6.

Avian Activity:   Piscivorous birds observed in the vicinity of the dam during the week included up to 13 seagulls and 15 cormorants.     

Project:  Lower Granite

Biologist(s):  Mike Halter and Ches Brooks 

Dates: September 14 - 20, 2012
Turbine Operation

Lower Granite had turbine units 1, 2, 3, and 5 available for power generation at the beginning of the report period.  Turbine unit 5 was taken out of service on September 17 at 0654 hours in support of cavitation repair with an indefinite return to service date.  Turbine unit 6 is out of service for annual maintenance, with a tentative return to service date of September 27.  Turbine unit 4 is out of service for cavitation repair with an indefinite return to service date.  Turbine unit 1 was out of service from 0807 to 1333 hours on September 19 in support of trash rack raking.  Turbine unit 2 was out of service from 1159 to 1358 hours on September 19 in support of trash rack raking efforts in slot 1C.  
Because of elevated descaling rates (as detailed below under the Juvenile Fish Facility section ), turbine units 2 and 3, were designated as the first and second turbine units in priority as of September 18.  Turbine unit 1 was placed in last on, first off priority.  Previously from September 6 to September 18, turbine unit 1 was operated in first priority since this unit provided additional attraction for the South Shore Adult Fishway Entrances (SSE 1 & 2).  Increased descaling rates appeared to coincide with the return of turbine unit 1 to service.  Because of current low river flow conditions, Unit 1 was operating at the upper end of the 1% efficiency curve.  Since this turbine unit has a fixed blade, the range of operation is more limited than is the case with an adjustable Kaplan blade.  These limitations may have cause excessive gatewell turbulence which in turn may result in increased descaling rates.   All operating turbine units were run within the 1% operation criteria during the week.
Adult Fish Passage Facility

On September 14, 15, and 19 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.    

Fish Ladder:   All criteria were met.  The differential between the forebay and the adult fish ladder exit ranged from 0.3 – 0.4 feet on inspections this week.   

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the weekly inspections.  The head differential reading at the north shore fishway entrances was slightly out of criteria during the September 19 inspection with a reading of 0.9 feet (criterion 1.0’ – 2.0’).

Weir depths at the south shore fishway entrances also met criteria during all weekly inspections.  The north powerhouse fishway entrances were on sill on all inspections this week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 6.1 to 6.7 feet.  Weir depths at the north shore entrances ranged from 4.5 to 6.1 feet during the weekly inspections.  North shore weir depths are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.97 to 1.09 feet per second and averaged 1.04 feet per second during the weekly inspections.

Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and three were run all week.
Juvenile Fish Passage Facility

On September 11, after observing elevated descaling rates, the Corps biologist notified the powerhouse Operator and with the Operator’s assistance inspected the orifices (these orifices are back flushed at least every three hours around the clock).  Unit 1 and 2 trash rack and VBS differentials, were also measured and found to be withing criteria.  The differentials were measured again on September 18 and again, all inspection points were within criteria.  No problems that would negatively impact fish at the Juvenile Fish Facility itself have been found to date. 

From September 6 to 20, 2012, a total of 3,215 fish were sampled for descaling – of these 303 were counted as descaled – for an average descaling rate of 9.4%.  As a limited comparison - during the same time period for the years 2009-2011 the average descaling rates were 5.6% of 5,259 fish sampled in 2011, 3.4% of 5,587 fish sampled in 2010 and 4.6% of 542 fish sampled in 2009.  The facility mortality rate averaged 1.4% for September 6 – 20, 2012 time period. 

 On September 19, project personnel raked the unit 1 trash racks, removing 3 loads of debris (approximately 30 cu yards total).  Fish sampling data became available on September 21 to evaluate the change from having Unit 1 reprioritized and the trashracks raked (after the close of this report period).  Descaling rates of 4.1 and 7.7% were respectively recorded for fish collected on September 20 and 21.  These descaling rates are higher than expected for this time of year, and late August descaling rates have been typically 2% or lower (descaling rates for late year, low fish number samples, have varied quite widely in the past).  Since descaling rates were higher than expected on September 20 and 21 when only turbine units 2 and 3 were operated, additional trash rack raking has been scheduled.
Forebay Debris/Gatewell Debris/Oil:  The amount of floating forebay debris increased to approximately 50 square yards this week; none was removed.   

ESBSs/VBSs:  VBS/ESBS video inspections last took place on August 24.  The next inspections are scheduled for October.              

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light at these points during the report week.  

Transportation Facility:  The JFF operated smoothly during the week (except for the increased descaling rate noted above).  There were no operational problems of any kind with fish collection, fish sampling, or fish transportation equipment.  Avian hazing activities concluded for the season on June 30.  The sample rate remained at 100% during this report period.
Transport Summary:  Every other day fish barging operations concluded on August 16.   All fish barges have been returned to Lower Granite and are docked for maintenance work and winter storage.  Fish trucking operations began on August 18 using the 300 gallon pickup mounted midi-tank.  Collected fish numbers remained relatively low this week and well within the capacity of this transport vehicle.   Starting September 5, Lower Granite began combined fish truck transport operations with Little Goose.  Combined transport operations with Little Goose will continue as long as fish numbers remain low.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.
River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	25.5
	21.7
	0.0
	0.0
	65.8
	65.5
	5.0
	4.5


*Scrollcase temperature.

Other
Visual adult fish ladder counts are taking place between the hours of 0400 and 2000.  Visual fish counts began on April 1 and are scheduled to continue through October 31.

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on August 29.  Only one possible lamprey mortality was found in the strainers over a combined run time of 676.5 unit hours.  The next cooling water strainer inspections are scheduled for late September.
Invasive Species:  The zebra mussel trap near the adult fishway exit was last examined on September 7.  No evidence of zebra mussels was found.  The next inspection is scheduled for early October.
Fish Salvage Operations:  Lower Granite Fish Facility personnel lead two fish rescue operations during the report week.  On September 17 and 18 a fish rescue took place in the turbine unit 2 draft tube at Dworshak Dam.  By the afternoon of the 18th this draft tube was successfully unwatered.  Lower Granite personnel entered the draft tube and recovered 1 juvenile clipped Fall Chinook.  This fish was released into the tailrace in perfect condition.  On September 19, the turbine unit 5 scrollcase was unwatered at Lower Granite Dam.  Two adult Bridge Lip suckers were recovered and released alive into the tailrace.  Both dewatering events took place in support of cavitation repair.  The outstanding support of both powerhouse crews was vital to the safe and successful completion of these activities.    
Research

Adult Fish Trap Operations:  Adult fish trap operations continued with a sample rate of 15%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes. 

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery and the Nez Perce Hatchery at Cherry Lane continued during the week.   The Nez Perce are trucking fish on Saturday and Sunday and Lyon’s Ferry Hatchery is trucking fish Monday – Friday.  Chinook jacks are being collected during the week and trucked to Lyon’s Ferry on Mondays.  Trucking operations will continue into November (or until hatchery needs are met).
National Marine Fisheries Service (NMFS) Late Season Subyearling Fall Chinook Transportation:   NMFS staff began PIT-tagging subyearling fall Chinook taken from the sample on September 6. The objective of this study is to assess the survival and returns of late season trucked and in-river subyearling fall Chinook. Approximately 50% of the marked fish will be transported and 50% will be bypassed to the river, 24 hours after recovering from PIT-tagging.

