U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#30-2012
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: September 21 - 27, 2012
Turbine Operation

McNary had 8 to 9 turbine units available for power generation this week.  Unit outages are recorded in Table 1.   On September 26, the project tested unit 14, operating it for 7.2 hours.  Maintenance determined that this unit needs to be unwatered on October 1 to address bearing issues.  All available units operated within the 1% efficiency criteria.   
Table 1.  Unit Outages at McNary Dam.

	Units
	Outage Dates
	Outage Length
	Reason

	3
	Jun 4 to Jan 30.
	8 months. 
	Rewind contract.

	8
	Jun 11 to Jan 30.
	8 months.
	 Rewind contract.

	11 and 12
	Sep 3 to Oct 25.
	3 months.
	Install digital relay.

	14
	Sep 18 to unknown.
	Unknown.
	High turbine bearing temperature.

	1
	Sep 24 to 27.
	3 days.
	Annual maintenance.


Adult Fish Passage Facilities

On September 21, 24 and 26, the McNary fisheries biologist performed measured inspections of the adult fishways.  Visual fish counts continued.  Video adult lamprey counts and the nightly lowering of SFEW1, SFEW2, NFEW2 and NFEW3 for lamprey passage will conclude September 30.          

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  Debris loads along the north shore remain low.  At the Oregon exit, screen differential monitoring revealed no problems.  Woody debris along the Oregon shore remains light and scattered with location dependent on wind direction.     
Fishway Entrances and Collection Channel:  Since the end of routine spill for fish passage, the project has been able to maintain entrance weir depth and calibration more consistently.     

All Washington ladder inspection points met criteria this week as did most Oregon ladder inspection points.   All week, south powerhouse entrance weir depths at SFEW2, measured between 8.7 to 8.9 feet.  On September 21, SFEW1 depth measured 8.9 feet.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential between 1.1 and 1.2 feet.  The north powerhouse pool differential measured 0.9 feet on September 24.  These readings are typical this time of year due to low tailwater elevations.  All other Oregon ladder inspection points met criteria.     

Collection channel velocities averaged 1.5 feet per second.  The permanently mounted velocity meter remains out of the water due to a shortened cable.  Until this can be resolved, surface velocity measurements will be taken manually. 

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile facility continued to provide the usual 450 cfs to the north powerhouse pool.  From September 26 to 27 (2330 to 0042 hours) the Wasco County PUD had one interruption in service.  No reason was recorded.  The bypass system functioned well during the outage.                        

Juvenile Fish Passage Facility

Truck transport continued this week with one interruption in collection.  On September 21, from 1700 to 1800 hours, the system was in primary bypass to allow the removal of algae from the flume section upstream of the separator.  For the report period, 6,415 smolts were collected along with 100 juvenile lamprey and 22,850 juvenile shad.  The transport season will conclude at 0001 hours on October 1 with the last truck trip occurring the same day.   

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was light and consisted of a mixture of wood and milfoil.  Location is affected by wind and project operations.  Facility staff monitored trash rack differentials with no problems found.  No racks were cleaned this week.  Two problems were found during gatewell inspections.  ESBS ropes were respectively removed from orifice inflows at slots 7A and 9B slots on September 22 and 26.    

ESBSs/VBSs: ESBSs are deployed in all turbine units except unit 3 which is out of service until January 2013.  ESBSs in slots 1A and 7C remain in transducer bypass mode.  On September 23, operators reset the ESBS cleaning brush travel distances in slot 1B following observations that the brush was not traveling to the end of the screen.  Later the same day, this screen was placed in transducer bypass mode.  On September 25, camera inspections took place at unit 1 as this unit was already out of service.  No problems were found.  

The fisheries staff found 7 VBSs exceeding differential criteria this week.  Six of these screens and 13 others were cleaned on September 21 and from September 23 to 27.  Slot 1A VBS differentials measured 1.5’ on September 23.  The operator “burped” the unit by taking it out of and into service.  Afterwards, the differential measured 1.1 feet.  This VBS was not cleaned this week as the unit was removed from service for maintenance the next day.  Following cleaning on September 25, the VBS in slot 13B was replaced with a rehabilitated screen.  Turbine unit 3 VBS slots are being used as staging areas during VBS swaps as the screens normally in this location are being rehabilitated.  As mentioned above, turbine unit 3 is out of service until January, 2013. 

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in use.   ESBS ropes impeded orifice flows on 2 occasions as mentioned above.  No fish injuries were noted in either case.  Because the ESBS rope in slot 7A was frayed, a biologist closed the slot’s south orifice and opened the north one.  On September 27, a technician found an orifice in slot 10C closed and immediately reopened it.  The facility staff was not able to determine why or how the orifice was left closed.  The longest possible closure duration would have been about 24 hours.  No unusual fish injuries were observed.  Biologists continued to open and close orifices associated with units 3 and 8 as needed in support of VBS rehabilitation efforts (these units are out of service).  These changes are needed to maintain proper collection channel elevations.
Unit 1 VBSs were covered with heavy debris before the unit was removed from service.  Because this unit was out of service for most of the week, the VBSs were not cleaned.  When the head gate work began, this debris sloughed off the VBSs and accumulated on the rectangular screen.  The fisheries staff’s quick reaction minimized the problem.  This was a rare event but in the future the project will try to clean VBSs before a unit returns to service.  In addition, another forebay debris removal operation will be scheduled before the tug (or “log bronc”) is returned to Lower Granite Dam.  Table 2 reflects the time line of events of September 27 when the rectangular screen was obstructed with debris during unit 1 headgate removals.

Table 2.  September 27 Time Line.

	1340
	Began raising unit 1head gates.

	1400
	Heavy debris noted at facility separator.

	1415 to 1620
	Fisheries staff to collection channel.  Found rectangular screen blocked with milfoil.  Swapped unit 1 orifices with spares at unit 2.  Ran rectangular cleaning device twice along with air burst system.  Cleared blockage.  Swapped orifices back.     

	1538
	Head gate work completed.

	1608
	Unit 1 returned to service.


For the most part, all systems operated well in automatic mode.  On September 21, a biologist noted that the rectangular screen cleaner was not completely raising the brush out of the water.  Maintenance staff determined that the limit switch was sticking.  Normal operation resumed after switch adjustments.  The electrical staff is scheduled to lubricate the switch.  As mentioned in previous reports, the transition screen cleaning brush remains out of service until a channel shutdown occurs.  

The backup compressor used to supply air to the rectangular screen air bubbler remains out of service as the powerhouse air supply continues to be very reliable.  The compressor had been running continuously due to a failed switch.  The compressor will remain off until the switch is replaced.

The fish facility staff plan to monitor the collection channel 24 per day, 7 days per week once fish collection and transport operations cease.  

Transportation Facility:  Collection for truck transport continued.  During collection, PIT tag detection occurred in the full flow bypass pipe and throughout the facility.  The primary (A and B) PIT tag slide gates remained in service and the secondary (C and D) PIT/bypass gates remained closed (and off) to facilitate the routing of fish to the raceways.  Water balloons were used to check for debris blockages within the PIT tag system.  No blockages were found.  Some scheduled minor maintenance occurred this week.  Fish collection for truck transport will conclude at 0001 hours on October 1 when the fall primary bypass season begins.      

Smolt monitoring occurred daily and sample gates remained on during collection.  When sample rates exceed 20 percent of the collection, the PIT tag system is placed in override mode.  This mode of operation allows the PIT tag gates to function when the sample gates are open.  When not in override mode, PIT tag gates do not function when the sample gates are open.     

The facility continued to have difficulties with the west raceway gantry crane.  On September 21, the crane stalled during truck loading, but was able to complete crowding operations.  On September 23 and 25, the gantry failed and the fisheries staff loaded the truck without the crane or the crowder.  Fortunately, hand crowding was feasible due to low debris loads and low fish numbers.  On September 24, repairs were attempted but not entirely successful.  The electrical staff resolved the issue permanently September 25 by replacing electrical gel compound within the gantry control system.  This gel conducts excessive heat away from electrical circuits, keeping them cool. 

On September 25, an additional computer was installed within the fish facility.              

Transport Summary:  Every other day trucking continued with trips occurring on September 12, 23, 25 and 27.  The last truck departure is scheduled to take place October 1.  On September 25, the biologist accompanied the driver to the release site.  Traffic congestion complicated the return trip in the Phillipi Canyon vicinity as people were trying to view bighorn sheep.  During the September 25 trip, fish releases were delayed 30 minutes as contractor equipment was blocking the truck pad.  Contractors are currently removing the salt water challenge research facility next to the Bonneville smolt monitoring facility.  The driver also recovered a single smolt mortality trapped between the inner and outer sections of the release pipe.  
River Conditions

River conditions during the week are outlined in Table 3 using data provided by the smolt monitoring staff.  The data day is from 0700 to 0700 hours.  The average spill recorded was in excess of powerhouse capacity, all occurring on a single data day.  On September 25, spill bay 13 was restored from split leaf to its normal configuration.  
Table 3.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity*

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	110.6
	89.9
	0.4
	0.0
	65.9
	64.6
	6.0
	     6.0


*Control room data.
Other
Inline Cooling Water Strainers:  The next main unit cooling water strainer examination will occur on October 2.     
Invasive Species:  The zebra mussel trap was examined September 23.  No invasive species were found.               

Avian Activity:  Corps technicians continued bird counts.  Tailwater high counts (exclusive of the bypass outfall) included 25 terns, 24 gulls, 4 cormorants and 2 mergansers.  Most of these were seen in the vicinity of the powerhouse.  Most of these birds are assumed to be feeding on shad.  The terns and the mergansers were observed only on a single day.  No birds were seen at the bypass outfall.  High forebay counts included 4 gulls and an occasional osprey, grebe or cormorant.  No grebes were observed anywhere else on project.  Gulls and cormorants continue to roost on the rocks by Washington shore boat dock.  APHIS hazing activity concluded August 4.  Bird counts are slated to end September 30.

The bypass outfall water cannon remained out of service.  Current plans are to install a second pump and complete walkway grating repairs during the late November to the end of December time period.  The propane hazing cannons continued to operate well.  

On September 26, a member of the Bonneville Fisheries Field Unit reviewed bird counting protocol and data entry with the McNary fish facility staff.  

Research:  The adult lamprey study is now the only onsite research in progress.  This work is taking place only at the ladder exits.  Contractors completed the removal of juvenile salmonid passage study equipment this week.  

On September 27, district personnel removed video cameras at the entrance and exit of the 80’ adult fallback return line between the separator and the recently constructed bypass outfall pipe.  This monitoring equipment was installed in response to NOAA Fisheries concerns regarding the potential for adult fish passage delays or injuries inside the return line.  Causal observations indicate no problems with adult passage.    

Project:  Ice Harbor

Biologist:  Mark Plummer 

Biological Technician:  Stephen Jeffers
Dates: September 21 - 27, 2012
Turbine Operation
Turbine units 1-3 were available for operation this reporting period.  Turbine units 1-3 were out of service for short periods September 24 while STS/VBS inspections were performed and on September 26 in support of transformer #6 work.  Turbine units 4-6 remain out of service and unwatered.

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fish passage ways September 25, 26, and 27.
Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  
Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.3 feet, off sill with a depth of 7.1 feet and off sill with a depth of 7.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 7.3 feet, off sill with a depth of 7.2 feet and off sill with a depth of 7.3 feet.  The north shore entrance (NSE) was on sill with a depth of 7.3 feet, off sill with a depth of 7.5 feet and off sill with a depth of 7.3 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  Channel/tailwater differential criterion is 1 – 2 feet.  All out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings ranged from 2.6 fps - 2.7 fps.  The channel velocity criterion is 1.5 fps – 4.0 fps.
Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Seven of 8 south shore fish pumps were operated without problems.  On September 20, south shore fish pump 4 was placed out of service at 0906 hours due to excessive gearbox oil leakage.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  

STSs/VBSs:  The STS screens are in cycle run mode.  No problems were found during the September 4 and 24 STS/VBS inspections.  October STS/VBS inspections are tentatively scheduled for October 22 and 24.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was placed in operation March 19.  Twenty orifices are open.  No problems to report.    
Juvenile Bypass Facility:  The bypass was placed into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill in support of fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	23.2
	10.0
	0.0
	0.0
	66
	64
	7.4
	6.8


*Unit 1 scrollcase temperature.
Other

Inline Cooling Water Strainers: Cooling water strainer inspections took place September 24 in turbine units 1, 2 and 3.  Although no lamprey were found, a total of 7 juvenile shad mortalities were recovered over a total operating time of 1,346 hours.  Units 4, 5 and 6 were not inspected as they are currently unwatered for maintenance. 
Invasive Species: No zebra mussels were observed during adult fishway inspections. 
Project:  Lower Monumental
Biologists: Bill Spurgeon and Elizabeth Lindsey
Dates: September 21 - 27, 2012
Turbine Operation

The units are being operated within hard constraint 1% operational criteria.  Unit 4 was removed from service at 0945 hours August 13 for six year annual maintenance and remained out of service through this period.  
Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC/State biologists on September 21, 22, 24, 25, and 26.   

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) during all inspections.  

Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.
SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 5.9’, 6.1’, 6.4’, 6.7’, and 6.5 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 6.8’, 7.4’, 7.2’, and 7.1 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

The collection channel velocity remained in criteria (1.5 - 4.0 ft/sec) this week. 

Auxiliary Water Supply System: All AWS pumps were in service and operating during this period. 

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 11.0 square yards of forebay debris observed during this report period.  Gatewell debris ranged from 0-22% surface coverage.  No oil was observed in the gatewells this week. 

STSs/VBSs:  STS operations remain in cycle run mode.  STSs were inspected on September 4, 5 and 6.   A row of loose clips was observed on the STS in gatewell slot 2B on September 4.  The screen was repaired as a preventative measure on September 5.    
Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.  The primary dewaterer automatic weirs remains set at 528.1 feet to eliminate sudden water level fluctuations in the separator.    

Collection Facility:  The facility is in collection for transport mode.  Facility mortality exceeded 6% on September 21, 22, 23, 24, 25, and 26.  Percent mortality was 13.3, 6.5, 11.8, 40.0, 11.1, and 40.0, respectively.  The average facility mortality rate this week was 12.9% (22 mortalities out of 170 juvenile salmonids collected).  Sampled sub-yearling Chinook had an average columnaris rate of 11.7% (17 infected out of 142 sampled).  As is facility standard procedure, each transport tank is treated with salt to ease fungal and bacterial infection.  No other problems occurred.  
Transport Summary:  Alternate day midi-tanker transport is occurring with trucks departing on odd numbered days this month.  The last truck of the season is scheduled to depart the facility on October 1. 
River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	20.1
	12.6
	0.0
	0.0
	65.5
	64.0
	5.0+
	4.6


 *Scrollcase temperatures.

Other

Summer spill operations ended at 0001 hours on September 1.  

Inline Cooling Water Strainers: Cooling water strainers were inspected on September 17.  No live lamprey were recovered.   Mortalities included 1 juvenile carp, 2 juvenile channel catfish, 3 Siberian prawns, 5 juvenile shad, and 1 undetermined species. 
Invasive Species: There were no zebra mussels observed at the monitoring stations on September 3.
Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls and cormorants were the prominent species observed.  Hazing ended on June 2. 
Project:  Little Goose

Biologist: George Melanson
Dates: September 21 - 27, 2012
Turbine Operation

Turbine units 1, 2, and 5 were available for service throughout this report period.  Turbine unit 6 was returned from service following exciter replacement on Sept 24, at 1800 hours.  Turbine unit 3 was returned to service following annual maintenance on September 26 at 1520 hours.  Turbine unit 4 remained out of service for exciter replacement.  On September 24, turbine unit 1 operated outside the 1% efficiency criteria from 1412 to 1436 hours (24 minutes).  Turbine unit 6 operated outside the 1% efficiency criteria due to exciter testing with 6 events on September 21 totaling approximately 2 hours and 4 events on September 24 totaling approximately 6.5 hours.

Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on September 21, 23, 25 and 27.
Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.1 and 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials remained steady at 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 0.9 and 1.8 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.2 and 8.7 feet (criteria ≥8.0 ft). NPE weirs rested on sill and depths ranged between 5.9 and 7.3 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 6.1 and 7.3 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.2 to 2.3 fps near the SSE and 2.1 to 2.5 fps near the NSE.   On September 25, with two pump operation, the collection channel subsurface water velocity measured 2.2 fps (criteria 1.5 to 4.0) near the NPE.  Due to 2 pump operations and decreasing channel to head differentials, NPE2 was raised and closed on September 27.

Auxiliary Water Supply System:  On September 24 from 1040 to 1255 hours, fish pump 2 was removed from service (unscheduled outage) to repair water leaks.  On September 25 at 0645 hours, fish pump 3 was removed from service (unscheduled outage) also to repair a water leak.  Following repairs, fish pump 3 was unable to restart and remained out of service.   During the pump outages, the remaining two pumps were operated at increased RPM to make up additional water to the fish collection channel.  On September 27 at approximately 1800 hours, NPE 2 was raised and closed to increase channel to head differentials.  

Juvenile Fish Passage Facility
Forebay Debris/Gatewell Debris/Oil:  Up to 800 square feet of debris floated in front of the unit intakes this week.      

Spillway Weir:  The spillway weir was not operated during this report period.  Summer spill for fish passage ended on September 1.

ESBS/VBS:  All differential measurements indicated no debris buildup.  All ESBS screens operated within criteria during this report period.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 18 open orifices.

Transportation Facility:  The facility continued collection for transport at 100% sample rates.  Smolt collection totaled 55 for the week.  Descaling and mortality rate for the period was 5.6% and 3.6% respectively.  

Transport Summary:  Due to low numbers of fish collected, Lower Granite continued transporting Little Goose Fish during this report period.  Salt in small concentrations of approximately 1 g/L is added to the midi-tank water to treat Columnaris disease and reduce stress.  All trucking operations were satisfactorily completed.  
River Conditions

River conditions during the week are outlined in Table 1.
Table 1.  River conditions at Little Goose Dam.
	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*
(oF)
	Water Clarity
(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	20.3
	13.7
	0
	0
	65.6
	65.3
	6+
	6.0


*Ladder temperature.

Other

Inline Cooling Water Strainers:  All cooling water strainers were inspected on September 19.  No fish were observed.   Cooling water strainers were not inspected during this report period.

Invasive Species:  The zebra mussel substrate trap was inspected on September 6.  No mussels were observed.  The next inspection is scheduled for October 6.

Avian Activity:   Piscivorous birds observed in the vicinity of the dam during the week included up to 15 seagulls, 14 cormorants and 2 grebes.     

Project:  Lower Granite

Biologist(s):  Mike Halter and Ches Brooks 

Dates: September 21 - 27, 2012
Turbine Operation

Lower Granite had turbine units 1, 2, and 3 available for power generation at the beginning of the report period.  Turbine unit 6 returned to service at 0945 hours on September 27, after annual maintenance was completed.  Turbine unit 5 is out of service for cavitation repair with an indefinite return to service date.  Turbine unit 4 is out of service for cavitation repair with an indefinite return to service date.   

Turbine unit 2 was out of service from 0655 to 1015 hours on September 24 in support of trash rack raking.  This unit was forced out of service at 2223 hours on September 24 as the fish screen (ESBS) in slot 2B became inoperable.  At 0843 hours on September 25 a clearance was taken out on this unit in order to pull, inspect and replace two of the unit’s fish screens – the unit was returned to service at 1601 hours that afternoon.  Turbine unit 3 was out of service from 0711 to 1238 hours on September 24 in support of trash rack raking and replacement of unit heaters.  

Because of elevated descaling rates (see “Juvenile Fish Passage Facility section below for details), turbine units 2 and 3, as of September 18, are being respectively operated as first and second turbine units in priority.  Unit 1 has been placed in “last on, first off” priority. Because this turbine unit has a fixed blade, the range of operation is more limited than is the case with an adjustable Kaplan blade.  These limitations may cause excessive gatewell turbulence which in turn may result in increased descaling rates.  All operating turbine units were run within the 1% operation criteria during the week.
Adult Fish Passage Facility

On September 22, 25, and 27 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  The September 27 inspection was conducted jointly with the ODFW biologist from Little Goose Dam.  

Fish Ladder:  All criteria were met.  The differential between the forebay and the adult fish ladder exit ranged from 0.3 – 0.4 feet during inspections this week.   

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the weekly inspections.  The head differential reading at the north shore fishway entrances was out of criteria during the September 27 inspection with a reading of 0.7 feet (criterion 1.0’ – 2.0’).

Weir depths at the south shore fishway entrances met criteria during all weekly inspections.  The north powerhouse fishway entrances were on sill on all inspections this week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 5.6 to 6.9 feet.  Weir depths at the north shore entrances ranged from 3.6 to 6.3 feet on the weekly inspections.  North shore weir depths are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  

Velocity readings in the adult fishway collection channel transition pool area ranged from 1.00 to 1.08 feet per second and averaged 1.04 feet per second during the weekly inspections.

Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps 1 and 3 were run all week.
Juvenile Fish Passage Facility

While the rate of descaling did moderate this week, efforts to identify possible causes of increased descaling rates at the project continued.  Trash racks for Turbine units 2 (in slots 2B & 2C) and 3 (all 3 slots) were raked on September 24 – negligible debris was encountered.  On September 26 from 1455 to 1535 hours the Juvenile Fish Facility was placed in partial primary bypass mode in order to lower the water level below the separator bars, allowing removal of the bars.  This inspection revealed that the separator was almost entirely clear - less than half a five gallon bucket of mostly shells and small sticks was removed.  This also gave facility personnel a chance to completely pressure wash the incline screen.  No problems that would negatively impact fish at the Juvenile Fish Facility have been found to date.

During the report period a total of 899 fish were sampled for descaling – of these 53 were counted as descaled – for an average descaling rate of 5.8%.  As a comparison - during the same time period for the years 2006-2010 the average descaling rate was 5.4%.  The facility mortality rate was 1.34% for the report week.   The juvenile fish facility sample rate remained at 100% during this week.        

Forebay Debris/Gatewell Debris/Oil:  The amount of floating forebay debris increased to approximately 350 square yards this week; none was removed.   

ESBSs/VBSs:  The most recent VBS/ESBS video inspections last took place on August 24.  The next inspections are scheduled for October.              

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light at these points during this report period.  

Transportation Facility:  The JFF operated smoothly during the week (except for the increased descaling rates noted above).  There were no operational problems of any kind with fish collection, fish sampling, or fish transportation equipment.  Avian hazing activities concluded for the season on June 30.  The sample rate remained at 100%.
Transport Summary:  Every other day fish barging operations concluded on August 16.  All fish barges have been returned to the Lower Granite moorage facility for maintenance work and winter storage.  Fish trucking operations began on August 18 using the pickup midi-tanker.  Collected fish numbers remained relatively low this week and well within the capacity of this transport vehicle.   Starting September 5, Lower Granite began combined fish truck transport operations with Little Goose.  Combined transport operations with Little Goose will continue as long as fish numbers remain low.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the fish passage season.  Mandatory spill operations in support of fish passage ended August 31.
River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	20.6
	15.5
	0.2
	0.0
	65.4
	66.2
	4.9
	4.6


*Scrollcase temperature.

Other
Visual adult fish counts at the adult ladder are taking place between the hours of 0400 and 2000.  Visual fish counts began on April 1 and are slated to continue through October 31.

Inline Cooling Water Strainers:  Cooling water strainers were inspected for lamprey entrainment on September 25.  No lamprey mortalities were found in the strainers over a combined run time of 965.3 unit hours.  The next cooling water strainer inspections are scheduled for late October.
Invasive Species:  The trap near the adult fishway exit was last examined for zebra mussels on September 7.  No evidence of zebra mussels was found.  The next inspection is scheduled for early October.    

Research

Adult Fish Trap Operations:  Adult fish trap operations continued with a sample rate of 15%.  Scale samples were taken from one out of every 25 hatchery steelhead.  All wild steelhead captured were PIT-tagged and had scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) had both scale and genetic samples taken for verification purposes. 

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery and the Nez Perce Hatchery at Cherry Lane continued during the week.   The Nez Perce are trucking fish on Saturday and Sunday and Lyons Ferry Hatchery personnel are trucking fish Monday – Friday.  Chinook jacks are being collected during the week and trucked to Lyons Ferry on Mondays.  Trucking operations will continue into November (or until hatchery needs are met).
National Marine Fisheries Service (NMFS) Late Season Subyearling Fall Chinook Transportation:   
NMFS staff began PIT-tagging subyearling fall Chinook taken from the sample on September 6.  The objective of this study is to assess the survival and returns of late season trucked and in-river subyearling fall Chinook.  Approximately 50% of the marked fish will be transported and 50% will be bypassed to the river, 24 hours after recovering from PIT-tagging.
