 U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#40-2012
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: November 30 – December 6, 2012

Turbine Operation

McNary had 9 to 10 units available for power generation this week.  On November 1, the soft one percent criterion began.  At times, units ran outside the criteria at the BPA’s requests.  Unit outages are recorded in Table 1.  

Table 1.  Unit Outages at McNary Dam.

	Units
	Outage Dates
	Outage Length
	Reason

	3
	Jun 4 to Jan 12.
	7.5 months. 
	Rewind contract.

	8
	Jun 11 to Jan 12.
	7.5 months.
	 Rewind contract.

	14
	Sep 18 to Jan 30.
	4.5 months.
	Turbine bearing.

	10
	Nov 27 to Jan 31.
	2 months.
	Turbine bearing. 

	2
	Dec 3.
	10.6 hours.
	Turbine bearing oil valve.

	13
	Dec 4 to 5.
	34.8 hours.
	Replace cooler.

	9, 11 & 12
	Dec 4.
	47 minutes.
	ESBS camera inspection.

	6
	Dec 5.
	7.6 hours.
	Tap hub.

	11
	Dec 6 to 7.
	25 hours, 3 outages.
	Exciter issues.


Adult Fish Passage Facilities

On November 30, December 2 and 5, the McNary fisheries biologist performed measured inspections of the adult fishways.  Video counts and monitoring of adult passage is in progress.  Video counts and monitoring will continue through February 28, except when the ladders are out of service for winter maintenance.     
Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  From December 2 to 5, project personnel replaced the upper limit switch on weir 335 near the Washington ladder exit.  Operators adjusted weir set points on December 5.  Oregon ladder exit monitoring revealed no problems and traveling screen differential measurements have been satisfactory.  Operators adjusted the Oregon ladder weir set points on December 2. 

Fishway Entrances and Collection Channel:  All Washington ladder inspection points and most Oregon ladder inspection points met criteria this week.  All week, both south powerhouse entrance weirs, SFEW1 and SFEW2, measured depths ranging from 8.3 to 8.5 feet.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.2 feet.  North powerhouse pool differentials measured between 0.7 and 0.9 feet.  On December 2, entrance weirs, NFEW2 and NFEW3, measured depths of 8.9 feet.  These north powerhouse readings are probably due to the juvenile system being in emergency bypass.  Collection channel velocities averaged 1.8 feet per second.  The new velocity meter cable was delivered this week.  The facility staff will schedule installation for a day when low tailwater elevations are expected. 

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with one interruption in service.  On December 5, from 1524 to 1600 hours, both pumps were out of service in support of fish pump house carbon dioxide fire suppression system tests.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile facility remains in emergency bypass and is no longer providing the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no interruptions in service this week.        

Juvenile Fish Passage Facility

Fall bypass season continues with the system in emergency bypass due to failure of the rectangular screen cleaning device in the collection channel.  The staff continued light maintenance at the facility which has been dewatered and winterized to avoid possible freeze breakage.         

Forebay Debris/Gatewell Debris/Oil:  Forebay debris concentrations were light to moderate, consisting of a mixture of wood and milfoil.  Debris distribution is mainly affected by wind direction.  The fisheries staff continued to monitor trash rack differentials and no problems were found.  No racks were cleaned.  Gatewell observations produced satisfactory results.

ESBSs/VBSs:  ESBSs are deployed in all turbine units except unit 3 which is out of service until January, 2013.  The screens in slots 1A, 1B and 7C remain in transducer bypass mode.  The ESBS in slot 7C was observed “short cycling” on December 5.  In this case, the cleaning brush reversed direction before reaching the top of the ESBS.  Normal brush operation was restored the same day after operators recalibrated the screen.  Camera inspections took place on December 4 in units 9, 11 and 12.  All inspected screens were in found satisfactory condition.  This week, the project moved two spare ESBSs to the storage yard and raised the screens associated with units 8, 10 and 14 which will be out of service past December 15.  ESBS rehabilitations continued.       

The fisheries staff continued to monitor VBS differentials this week, finding no screens out of criteria even with units running at higher electrical loads.  As a preventative measure, the project cleaned a total of ten screens on November 30 and December 3.  VBS rehabilitations continued.          

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  This week, 42 orifices were in use and no problems were observed.  Because the ESBS rope in slot 7A is frayed, the slot’s south orifice remains closed and the north one is open.  Emergency bypass operations continued with all systems out of service.  The replacement clutch bearing for the rectangular dewatering screen cleaning device will be custom built in Japan.  The earliest possible delivery date is December 13.

Transportation Facility:  Scheduled facility maintenance continued.  All systems remain shutdown as smolt monitoring has ended for the season.  Work continued on the bypass line access walkway near the separator.  Project welders have begun rebuilding the porosity control screens.  The facility staff has begun to replace 2 truck flume driers and 2 raceway supply valve actuators.      

Transport Summary:  Fish transport operations have ended for the season.

River Conditions

River conditions during the week are outlined in Table 2.  Reported data was compiled from COE websites and the control room.  The data day is from 0000 to 2400 hours.  Spill in excess of powerhouse capacity began December 6.                 

Table 2.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	175.8
	131.9
	19.9
	0.0
	49.0
	48.0
	6.0
	     6.0


Other

Inline Cooling Water Strainers:  Project personnel performed main unit cooling water strainer examinations on December 4.  Three juvenile lamprey mortalities were recovered from turbine units 7 and 9.  Juvenile shad mortalities were also recovered.               
Invasive Species:  Zebra mussel traps are slated for examination in late December.      

Avian Activity:  Bird counts and hazing are no longer occurring.  Casual observations are still being taken during fishway inspections.  Cormorants and gulls continue to be observed in tailwater locations.  Most cormorants were roosting on the navigation lock wing wall.  The gulls were also roosting or were feeding in the powerhouse flow.  Mergansers are also occasionally observed.  On December 5, a raft of mergansers were seen just downstream of spill.    Bird numbers appear to be fluctuating with outmigration of juvenile shad.  Migrating birds may be temporarily in the area at times, which can affect observation results.  Emergency bypass outfall observations included gulls and an occasional cormorant or merganser.  Forebay observations included an occasional gull, cormorant, a raft of gulls, or group of grebes.  Gulls continued to be seen occasionally on the rocks by the Washington boat dock.

The bypass outfall water cannon remained out of service.  Contractor personnel are currently repairing walkway gratings.  Pump installation will follow the walkway grating repairs.  New pump installation is expected by the third week of December.       

Research:  No research is occurring at this time. 
Project:  Ice Harbor

Biologist:  Mark Plummer 

Dates: November 30 – December 6, 2012

Turbine Operation

Turbine units 1, 3, and 4 were available for operation this reporting period.  Turbine units 2, 5, and 6 remain out of service.  Turbine units 1 and 3 were out of service for a short period on December 3 to remove juvenile shad from plugged cooling water strainers.  On December 4, turbine unit 4 was briefly taken out of service for the same reason. 

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fish passage ways December 3, 4, and 5.

Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north and south adult fish ladder picketed leads were raised November 1. 

Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with 8.4 feet depth, off sill with 8.6 feet depth, and off sill with 8.4 feet depth. The north powerhouse entrance (NFE) was on sill with 8.7 feet depth, on sill with 9.2 feet depth, and on sill with 9.5 feet depth. The north shore entrance (NSE) was off sill with 8.5 feet depth, off sill with 8.6 feet depth, and off sill with 8.6 feet depth.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth or on sill at 332.25 per the Fish Passage Plan.  Channel/tailwater differential criterion is 1 – 2 feet.  Out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings were 2.7 fps, 2.3 fps, and 2.5 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Six of the 8 south shore fish pumps were operated without problems.  South shore fish pump 4 remained out of service due to excessive gearbox oil leakage.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  

STSs/VBSs:  The STS screens are in cycle–run mode.  No problems were found during the November STS/VBS inspections.  All STSs are scheduled to be removed by December 19.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The Juvenile Fish Bypass was placed in operation March 19 with 20 orifices open.  The power supply cord for the screen cleaner is wearing, exposing individual wires.  The screen cleaner was returned to full operating service November 29 at 0750 hrs. 

Juvenile Bypass Facility:  The bypass was placed into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Mandatory spill in support of fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	42.9
	19.3
	0.0
	0.0
	66
	50
	6.4
	4.8


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Individual fish from the juvenile shad out migration are plugging turbine unit cooling water strainers.  No lampreys are being found in the strainers.  

Invasive Species:  No zebra mussels were observed during adult fishway inspections.  

Project:  Lower Monumental

Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: November 30 – December 6, 2012

Turbine Operation

All available turbine units are being operated within the soft 1% constraint criteria.  Unit 2 was taken out of service for annual maintenance at 0713 hours on December 3.  Unit 3 was taken out of service from 0728 to 1241 hours on December 3 in support of an intake gate cylinder swap.
Adult Fish Passage Facility

The adult fishway was inspected by fish facility personnel on December 3, 4, and 5.   

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The adult fish counting season ended on October 31.  North ladder picketed leads were raised on November 1.  South ladder picketed leads were raised on November 15. 

Fishway Entrances and Collection Channel:  NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 6.9’, 6.9’, and 5.8 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.9’, 7.5’, and 6.8 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Collection channel velocity was in criteria (1.5 - 4.0 ft/sec) this week. 

Auxiliary Water Supply System:  AWS pumps were rotated out of service for scheduled maintenance on November 21.  AWS pump 2 was removed from service at 0940 hours on November 21 for bearing repair and shaft alignment.  Two pump operation will continue until work on pump 2 is complete, approximately April 15.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 143.3 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-50% surface coverage.  No oil was observed in any of the gatewells this week. 
STSs/VBSs:  STS operations remain in cycle-run mode.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.  

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	44.4
	18.9
	0.0
	0.0
	47.5
	46.5
	4.4
	4.0


*Scrollcase temperatures.

Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on December 3.  No live lamprey were recovered.   Mortalities included 263 juvenile shad. 

Invasive Species:  There were no zebra mussels observed at the monitoring stations on December 5.

Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls, grebes, and cormorants were the prominent species observed.  Hazing ended on June 2. 

Project:  Little Goose

Biologist: George Melanson
Dates: November 30 – December 6, 2012

Turbine Operation

Turbine units 1 and 4 - 6 were available for service for most of the report period.  Unit 2 remained out of service due to field ground errors.  Unit 3 was removed from service on November 16 for planned maintenance and exciter replacement. Turbine unit 5 was returned to service following exciter repairs on November 30 at 1138 hours.  Turbine unit 6 was forced out of service due to exciter failure from December 5 at 0647 hours to December 6 at 1650 hours.   All available turbine units were operated within the 1% efficiency criteria.

Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on December 3, 4 and 5.

Fish Ladder:  The ladder exit head differentials held steady at 0.0 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.1 and 1.2 feet (criteria 1.0-1.3 ft.)  Picketed leads were removed for the season on November 6.  No debris was observed at the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.4 and 1.6 feet (criteria 1.0 to 2.0 ft.). SSE weir depths ranged between 8.2 and 8.4 feet (criteria ≥8.0 ft). Depths for NPE1 ranged between 7.2 and 7.3 feet (criteria ≥7.0 ft or on sill). As a result of 2 pump operations and decreased channel to head differentials, NPE2 was closed on September 27.  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.4 and 7.9 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.3 to 1.5 fps near the SSE and 1.9 to 2.3 fps for inspections near the NSE.  Monthly subsurface water velocity was measured on December 3 near the north powerhouse entrance.  Measurements were attained near the surface, mid-depth and near the bottom.  The average velocity measured 3.0 fps with 2 pump operation. 

Auxiliary Water Supply System:   Fish Pump 3 has been out of service since September 25.  Repairs will be performed during the winter maintenance season.  Fish pumps 1 and 2 operated satisfactorily at increased speeds (RPMs) to provide additional water to the fish collection channel. 

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 5,000 square feet of debris floated in front of the unit intakes.   

Spillway Weir:  The weir was not operated this week.  Spill in support of fish passage ceased September 1.

ESBS/VBS:   All ESBSs operated within criteria during the report period.  Monthly manual operation/inspection of ESBS associated with turbine units 1, 2 and 4 - 6 were performed on December 3.  All inspected screens were in satisfactory working order. 

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 18 open orifices.

Transportation Facility:  Facility is being operated in primary bypass mode. All fish are being routed to the tailrace mid-channel area.  Maintenance work at the facility is in progress.   

Transport Summary:  Fish transport ended on October 31. 
River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	40.4
	18.5
	0
	0
	46.6
	46.1
	6.0
	6.0


*Ladder temperature.

Other

Inline Cooling Water Strainers:  All cooling water strainers were inspected on December 5.  No fish were observed.

Invasive Species:  The zebra mussel substrate monitor was inspected on November 6.  No mussels were observed.  The next inspection is scheduled for December 10.

Avian Activity:   Piscivorous birds observed in the vicinity of the dam during the week included up to 38 seagulls and 19 cormorants.     

Project:  Lower Granite

Biologist(s):  Mike Halter and Ches Brooks 

Dates: November 30 – December 6, 2012

Turbine Operation

Lower Granite had turbine units 1, 3, 4 and 6 available for power generation during this report period.  Turbine unit 2 is out of service for annual maintenance.  The expected return to date for this unit is December 14.  Turbine unit 5 is out of service for cavitation repair.  The tentative return to service date for this unit is March 13, 2013.  All operating turbine units were run within the soft 1% operational criteria during this report period.

The Lower Granite forebay operating range has been increased to 735.0 – 736.0 feet as a soft constraint and 735.0 – 738.0 as a hard constraint.   

Adult Fish Passage Facility

On November 30 and December 1, 2, and 5 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  

Fish Ladder:  All criteria were met.  An oil sheen was detected at the Lower Granite forebay on the morning of December 4.  Some of the sheen made it down the fishway ladder and through the fishway system (see “Other” section at the end of this report for details).  

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all fishway entrances during the weekly inspections.    

Weir depths at the south shore fishway entrances met criteria during all weekly inspections.  The north powerhouse fishway entrance weir depths either met criteria or were on sill dependent on the tailwater elevation.  Weir depths at the north powerhouse entrances ranged from 7.1 to 8.1 feet on this week.  Weir depths at the north shore entrances ranged from 4.7 to 7.6 feet during the weekly inspections.  North shore entrance 2 has been manually dogged off at 628.5 feet which is creating more weir depth than necessary at the loss of head differential.  North shore entrance 1 has not been adjusting its elevation adequately in auto mode to compensate relative to the fixed gate.  North shore weir depths are normally sacrificed in order to maintain the requisite 1.0 foot of head differential.

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.97 to 1.17 feet per second and averaged 1.07 feet per second during the weekly inspections.

Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps 2 and 3 were run all week.    

Juvenile Fish Passage Facility

The juvenile fish collection system was operated in the secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  The system is scheduled to operate in that mode through December 15 if weather conditions permit.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed. 

ESBSs/VBSs:  VBS/ESBS video inspections last took place on October 26 and 4 of the screens in units 2, 4 and 6 had issues with either missing rivets or loose straps with sticks behind them.  These problems will be addressed as soon as possible.                

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were back-flushed at regular 3 hour intervals all week.  Debris levels remained light at these points during the report week. 

 Transportation Facility:  The facility operated in secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  This activity will continue until December 15 (weather permitting).  The separator complex is still being manned 24/7 due to fish being routed over the separator bars.  No PIT-tag detection system is available at Lower Granite unless fish are diverted through the separator.  Operation of the separator in secondary bypass mode will allow the detection of PIT-tagged juvenile fish (primarily subyearling Chinook) and help determine late season movement patterns.

Transport Summary:  All transport operations concluded on October 31.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	45.4
	19.1
	0.0
	0.0
	48.8
	46.7
	5.0
	4.2


*Scrollcase temperature.

Other

Visual fish counting began on April 1 and continued through October 31.  Since November 1, video fish counting has been taking place on a daily basis between the hours of 0600 – 1600.  Video counts are slated to continue until approximately December 17. 

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey on November 28.  One lamprey mortality (unit 3, north strainer) was found in the strainers over a combined run time of 1,079.2 unit hours.  The next cooling water strainer inspections are scheduled for late December.

Invasive Species:  The zebra mussel substrate trap near the adult fishway exit was examined for zebra mussels on December 2.  No evidence of zebra mussels was found.  The next inspection is scheduled for March 2013.  

Oil Sheen:  An oil-like sheen was detected on the water surface of the Lower Granite forebay on the morning of December 4.   Some of the material (composition unknown at this writing) passed down through the fishway system.  An accumulation was noted in the tailrace spillway area.  Powerhouse crews placed oil soaker boom materials from the north powerhouse fishway exit wall over to the navigation lock wall.  The boom material remained in place overnight and was removed early on the afternoon of December 5.  An oil skimmer was also utilized to pick up remaining traces of the material.   

Research

 Adult Fish Trap Operations:  Adult fish trap operations have concluded for the season.  The adult trap was dewatered and winterized on November 19.   

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery has concluded for the season.  The last truck trip to Lyon’s Ferry took place on November 9.
