 U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

FISH FACILITIES WEEKLY REPORT

#43-2012
Project:  McNary

Biologists: Carl Dugger and Bobby Johnson
Dates: December 21 - 27, 2012

Turbine Operation

McNary had 10 units available for power generation this week.  Unit 8 was tested on December 22, 26 and 27.  On November 1, the soft one percent criterion began.  At times, units ran outside the criteria at the BPA’s requests.  Unit outages are recorded in Table 1.  

Table 1.  Unit Outages at McNary Dam.

	Units
	Outage Dates
	Outage Length
	Reason

	3
	Jun 4 to Jan 12.
	7.5 months. 
	Rewind contract.

	8
	Jun 11 to Jan 12.
	7.5 months.
	 Rewind contract.

	14
	Sep 18 to Jan 30.
	4.5 months.
	Turbine bearing.

	10
	Nov 27 to Jan 31.
	2 months.
	Turbine bearing. 

	1, 2 & 13
	Dec 21.
	In and out of service, 19 minutes, 5.0 hours & 3.3 hours.
	Model validation testing.

	1
	Dec 27.
	10.1 hours.
	Air cooler temperature device and piping installed.


Adult Fish Passage Facilities

On December 21, 23 and 26, the McNary fisheries biologist performed measured inspections of the adult fishways.  Video counts and monitoring of adult passage are in progress.  Video counts and monitoring will continue through February 28, except when the ladders are out of service for winter maintenance.  
Fish Ladders:  Both ladders met all Fish Passage Plan Criteria during measured inspections.  At the Washington exit, the general maintenance staff continued to regularly clean tumble weeds from the trash racks.  One low alarm was triggered this week.  Normal operation resumed after the operators reset the alarm and adjusted the set points.  Oregon ladder exit monitoring results have been satisfactory as have been traveling screen differential measurements.  However, tumbleweeds are being observed along the shore near the exit.      

Fishway Entrances and Collection Channel:  All Washington ladder inspection points met criteria.  Entrance weirs continued to drift in and out of calibration possibly due to the current spill.   All week, south powerhouse entrance weirs, SFEW1 and SFEW2, measured depths ranging from 8.1 to 8.3 feet and 8.2 to 8.5 feet, respectively.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential between 1.0 and 1.2 feet.  On December 21, the north powerhouse entrance weir depth measured 8.9 feet.  This reading is probably due to the juvenile system being out of service.  All other inspection points were in criteria.  Collection channel velocities averaged 1.6 feet per second.  The new velocity meter cable will be scheduled for installation during a day with low tailwater elevation in January.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile facility remains out of service and is no longer providing the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had one interruption in service on December 21, from 1212 to 1317 hours.  The reason for the outage was not recorded.  The bypass system operated well during this outage.        

Juvenile Fish Passage Facility

Collection channel maintenance is in progress.  Maintenance at the previously winterized sampling and holding facility continued.  

Forebay Debris/Gatewell Debris/Oil:  Forebay debris concentrations were light to moderate, consisting of a mixture of wood, tumbleweeds and milfoil.  Debris distribution is mainly affected by wind direction.  The fisheries staff continued to monitor trash rack differentials.  No problems were found and no racks were cleaned.  Trash rack differential monitoring will continue through the winter.  In early January, four trash racks will be cleaned per the Fish Passage Plan.  All gatewells were in satisfactory condition this week except for slot 10C which remains dewatered.   

ESBSs/VBSs:  All ESBSs are currently raised.  Winter maintenance and VBS rehabilitations are in progress.  Fish facility staff will resume VBS differential monitoring in April when the ESBSs are reinstalled.
Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: Orifices remain closed for winter maintenance.  All systems are dewatered and out of service.  The repairs to the transition and rectangular screen cleaning devices along with other maintenance will occur.  We continue to note moisture in some of the channel air lines.  On December 27, a contractor began the replacement of the three metal forebay bulkheads facing the channel with concrete.               

Transportation Facility:  Winter maintenance continues.  All systems remain dewatered and shutdown. Project welders continued rebuilding the porosity control screens.  The facility staff has completed the replacement of the 2 truck flume driers, the 2 raceway supply valve actuators and 6 flush line valves.  

Transport Summary:  Transport activity has ended for the season.         

River Conditions

River conditions during this report period are outlined in Table 2.  Reported data was compiled from COE websites and the control room.  The data day is from 0000 to 2400 hours.  For part of the week, spill in excess of powerhouse capacity occurred. 

Table 2.  River conditions at McNary Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	174.2
	133.2
	19.1
	0.0
	44.0
	43.0
	6.0
	     6.0


Other

Inline Cooling Water Strainers:  Main unit cooling water strainer examinations are scheduled for early January.  

Invasive Species:  The zebra mussel traps were examined December 23.  No invasive species were observed.      

Avian Activity:  Formal bird counts and hazing are no longer taking place. During fishway inspections, cormorants and gulls were observed in the tailwater area along with an occasional pelican.  Most cormorants were roosting on the navigation lock wing wall.   Gulls were also seen roosting in the navigation lock wall or feeding in the powerhouse or spill flows.  Bird numbers appear to be fluctuating with outmigration of juvenile shad.  Migrating birds may be temporarily in the area at times, which can affect observation results.  No birds have been observed at the bypass outfalls since December 20 when the bypass system was shut down. 
Only an occasional gull or grebe was noted in forebay locations this week.  Birds are no longer being seen on the rocks by the Washington boat dock.

Research:  There is no research is in progress at this time.   However, research plans are being formulated for next spring.

Project:  Ice Harbor

Biologist:  Mark Plummer 

Dates: December 21 - 27, 2012

Turbine Operation

Turbine units 1, 2, 3, and 4 were available for operation this reporting period.  Turbine units 2 returned to service December 27 at 1349 hours.  Turbine units 5 and 6 remain out of service.  

Adult Fish Passage Facilities

Fish facility personnel inspected the adult fish passage ways December 26.  Powerhouse operators inspected the passage ways daily.

Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north and south adult fish ladder picketed leads are raised.  Adult fish counting is to resume March 1, 2013.   Construction on a new replacement adult fish trap located in the south fish ladder is scheduled to be completed during the south fish ladder winter maintenance outage.

Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with 6.2 feet depth. The north powerhouse entrance (NFE) was on sill with 7.1 feet depth. The north shore entrance (NSE) was on sill with 7.1 feet depth.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth or on sill at 332.25 per the Fish Passage Plan.  Channel/tailwater differential criterion is 1 – 2 feet.  Out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings were 2.8 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Six of 8 south shore fish pumps were operated without problems.  South shore fish pump 4 remaind out of service due to excessive gearbox oil leakage.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  

STSs/VBSs:  All STSs are raised and stored in the “dogged” position.  No problems were found during the November STS/VBS inspections. 

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  All orifices are closed.  The dewatering structure and bypass pipe have been unwatered for the winter.

Juvenile Bypass Facility:  The bypass was unwatered for annual maintenance December 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill in support of fish passage ended September 1.  The RSW is currently not operating.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Ice Harbor Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	31.1
	19.1
	0.0
	0.0
	44
	42
	7.0
	6.6


*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Juvenile shad are plugging cooling water strainers during the course of their outmigration.  No lamprey are being found in the strainers during cleaning.  

Invasive Species:  No zebra mussels were observed during adult fishway inspections.  

Project:  Lower Monumental

Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: December 21 - 27, 2012

Turbine Operation

All units are being operated within the soft constraint 1% efficiency criteria.  Unit 6 deviated from 1% criteria from 1120-1131 hours on December 24 during BPA requested unit limit testing. 
Adult Fish Passage Facility

The adult fishway was inspected by fish facility personnel on December 26.   

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) during all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The adult fish counting season ended on October 31.  North and south ladder picketed leads were raised on November 1 and November 15, respectively.  

Fishway Entrances and Collection Channel:  NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth reading was 6.1 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) during all inspections.

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth reading was 7.2 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Collection channel velocity met criteria (1.5 - 4.0 ft/sec) this week. 

Auxiliary Water Supply System:  The system was in 2 pump operation during this period.  Two pump operation will continue until work on pump 2 is complete, approximately April 15.  

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 400.0 square yards of forebay debris observed during this period.  No oil was observed in gatewells this week. 
STSs/VBSs:  Unit 2 STSs were raised December 13.  The remaining STSs were raised for winter maintenance on December 17, 18, and 19.  

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass system was dewatered for winter maintenance on December 17.

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.  

Table 1.  River conditions at Lower Monumental Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature

(oF)*
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	30.9
	21.0
	0.0
	0.0
	41.0
	41.0
	3.9
	3.9


 *Scrollcase temperatures.

Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on December 3.  No live lamprey were recovered.   Mortalities included 263 juvenile shad. 

Invasive Species:  There were no zebra mussels observed at the monitoring stations on December 5.

Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls, grebes, and cormorants were the prominent species observed.  Hazing ended on June 2. 

Project:  Little Goose

Biologist: George Melanson
Dates: December 21 - 27, 2012

Turbine Operation

Turbine units 1, 4, 5 and 6 were available for service throughout most of this report period.  Unit 2 remained out of service due to field ground errors.  Unit 3 was removed from service on November 16 for planned maintenance and exciter replacement.  Unit 6 was forced out of service on December 27 at 2100 hours due to exciter failure.  All available turbine units were operated within the 1% efficiency criteria.

Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on December 26 and 27.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs held steady at 1.1 feet (criteria 1.0-1.3 ft.)  Picketed leads were removed for the season on November 6.  No debris was observed at the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.4 and 1.5 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths held steady at 8.3 feet (criteria ≥8.0 ft).  Depths for NPE1 ranged between 6.7 and 7.1 feet (criteria ≥7.0 ft or on sill).  As a result of two pump operations and decreased channel to head differentials, NPE2 was closed on September 27.  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.2 and 7.5 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.2 to 1.5 fps near the SSE and held steady at 2.1 fps near the NSE.  Monthly subsurface water velocity was measured on December 3 near the north powerhouse entrance.  Measurements were attained near the surface, mid-depth and near the bottom.  The average velocity measured 3.0 fps with 2 pump operation.

Auxiliary Water Supply System:  Fish Pump 3 has remained out of service since September 25.  Repairs will be performed during the winter maintenance season.  Fish pumps 1 and 2 operated satisfactorily at increased speeds (i.e.: RPMs) to make up additional water to the fish collection channel.

Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 300 square feet of debris floated in front of the unit intakes.   

Spillway Weir:  The weir is not in operation at this time. 

ESBS/VBS:   All ESBSs are raised and removed from service.  Visual inspections of the screens show all screens to be in good operating order.  No problems observed.  

Orifices, Collection Channel, Dewatering Structure, Flume: The juvenile collection system was dewatered for the season on December 17.

Transportation Facility:  The facility is dewatered and maintenance work is in progress.

Transport Summary:  Fish transport ended on October 31. 
River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	29.0
	19.0
	0
	0
	40.9
	40.7
	6.0
	5.0


*Ladder temperature.

Other

Cooling Water Strainers:  All cooling water strainers were inspected on December 27.  Recoveries included 45 lamprey mortalities.

Invasive Species:  The zebra mussel substrate monitor was inspected December 10.  No mussels were observed.

Avian Activity:  All counting activity has ended for the season.

Project:  Lower Granite

Biologist(s):  Mike Halter and Ches Brooks 

Dates: December 21 - 27, 2012

Turbine Operation

Lower Granite had turbine units 1, 2, 3, 4 and 6 available for power generation at the beginning of the report period.  Turbine unit 5 is out of service for cavitation repair with an expected return to service date of March 14, 2013.  

The Lower Granite forebay operating range has been increased to 735.0 – 736.0 feet as a soft constraint and 735.0 – 738.0 as a hard constraint.  Effective on December 18, and extending though the month of February, Lower Granite (and the other Snake Plants) have been authorized to operate at zero generation for up to a six hour time period (from 2200 – 0600 hours).

Adult Fish Passage Facility

A  measured inspection of the adult fishway system was conducted by a COE project biologist on December 14.   That inspection concluded the formal fishway inspections for 2012 at this facility.  The fish pumps were shut off at around noon on December 16.   Fish salvage operations in the adult fishway complex began on December 18.  The earlier than normal shutdown of the adult fishway system is to help expedite installation of new diffuser gratings and lamprey orifice structures.

Fish Ladder:  All criteria were met on the December 14 inspection.    

Fishway Entrances and Collection Channel:  The adult fishway system was dewatered for the winter starting on December 18.  

Juvenile Fish Passage Facility

The juvenile fish collection system was operated in the secondary bypass mode (all fish routed back to the river through the mid-river release pipe until the morning of December 20).  The juvenile fish collection gallery and separator were dewatered for the season on December 20, following final ESBS removal operations on December 19.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed. 

ESBSs/VBSs:  VBS/ESBS video inspections last took place on October 26 and four of the screens in Units 2, 4 and 6 had issues with either missing rivets or loose straps with sticks behind them.  These problems will be addressed as soon as possible.    The JFF staff will attempt to conduct video inspections early in 2013 to assess the condition of these screens.            

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals until the morning of December 20 when the system was shut down for the winter.

Transportation Facility:  The facility operated in secondary bypass mode until the morning of December 20.  Operation of the separator in secondary bypass mode allowed for the detection of PIT-tagged juvenile fish (primarily subyearling Chinook) and should help determine late season movement patterns.

Transport Summary:  All transport operations concluded on October 31.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.

River Conditions

River conditions during the week are outlined in Table 1.


Table 1:  River conditions at Lower Granite Dam.

	Daily Average

River Flow (kcfs)
	Daily Average

Spill (kcfs)
	Water Temperature*

(oF)
	Water Clarity

(Secchi disk - feet)

	High
	Low
	High
	Low
	High
	Low
	High
	Low

	30.4
	19.4
	0.0
	0.0
	---
	---
	N/A
	N/A


*Scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey on November 28.  One lamprey mortality (unit 3, north strainer) was found in the strainers over a combined run time of 1,079.2 unit hours.  The next cooling water strainer inspections are scheduled for late December.

Invasive Species:  The zebra mussel substrate near the adult fishway exit was last examined for zebra mussels on December 2.  No evidence of zebra mussels was found.  The next inspection is scheduled for March 2013.  

Adult Fish Counting:  Visual fish counting began on April 1 and continued through October 31.  Starting on November 1 and running through December 15, video fish counting took place on a daily basis between the hours of 0600 – 1600. 

Fish Salvage Operations:  Fish salvage operations took place in the adult fish ladder system on December 18 and 19.  The adult fish ladder section (ladder to collection channel) was dewatered on December 18.  The powerhouse collection channel section was dewatered on December 19.  The spillway section of the collection channel was not drained due to concerns with a problem bulkhead. 

The following fish were salvaged from the ladder section of the fishway:  112 adult American shad, 1 wild rainbow trout, 1 wild steelhead smolt, 2 wild Chinook smolts.  The large number of American shad were a bit of a surprise.  All of the shad were concentrated in a corner pool near the ladder exit.  Persons conducting the salvage removed as many as possible on the morning of December 18.  Due to concerns with other fish in the ladder, some shad were left in the corner pool of the fishway (with sufficient seepage water to hold them) until the rest of the ladder could be salvaged.  The last of the shad in the ladder section were removed (all alive) on the afternoon of December 19.

The following fish were removed from the powerhouse portion of the adult fishway:  7 adult hatchery steelhead, 2 bridge-lipped suckers, 1 peamouth, 9 juvenile wild Chinook.  These fish were loaded into a pickup tanker and released alive at Offield Landing.

Research

Adult Fish Trap Operations:  Adult fish trap operations have concluded for the season.  The adult trap was dewatered and winterized on November 19.   

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery has concluded for the season.  The last truck trip to Lyon’s Ferry took place on November 9.

